## Sheet1
Steam Blow Design Case Information:
| Pipe Evaluated |  | Unit HRSG Outlet Header
| Case |  | Case S-010
| Flow | lbm/hr | 1059212.3318 |  |  |  | Root Diameter | in | 1.5
| Pressure | psia | 1327.5041 |  |  |  | Tip Diameter | in | 1.25
| Temperature | °F | 1089.3025 |  |  |  | Fillet Radius at Base | in | 0
| Density | lbm/ft^3 | 1.5086 |  |  |  | Bore | in | 0.26
| Force | lbm ft^3/hr^2 | 743686740278.9083 |  |  |  | Unsupported Length | in | 2.5
| NPS | in | 16 |  |  |  | Minimum Wall Thickness | in | 0.25
| Schedule |  | 2.125
| ID | in | 11.75
| Area | ft^2 | 0.75301
| CFR Min |  | 1.05
| Press = | 100 | psia | [18 empty] | Press = | 125 | psia | [18 empty] | Press = | 150 | psia | [18 empty] | Press = | 175 | psia | [18 empty] | Press = | 200 | psia | [18 empty] | Press = | 225 | psia | [18 empty] | Press = | 250 | psia | [18 empty] | Press = | 275 | psia | [18 empty] | Press = | 300 | psia | [18 empty] | Press = | 325 | psia | [18 empty] | Press = | 350 | psia | [18 empty] | Press = | 375 | psia | [18 empty] | Press = | 400 | psia | [18 empty] | Press = | 425 | psia | [18 empty] | Press = | 450 | psia | [18 empty] | Press = | 475 | psia | [18 empty] | Press = | 500 | psia
| Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow |  |  |  | Thermowell |  |  |  | Thermowell |  |  | Thermowell |  |  | Thermowell |  |  | Steam Blow |  |  |  | Steam Blow
Temp | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a) |  |  | V.cn | V.max | (fps) |  | V.ratio | (n/a) |  | V.basis | (n/a) |  | Mass Flow | (pph) |  | Operating | Mass Flows | (pph) |  | CFR | (n/a)
(°F) | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | (fps) | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8 | Min | 0.4 | 0.6 | 0.8
330 | 1784.7754 | 713.9102 | 1070.8653 | 1365.8128 | 0.4 | 0.6 | 0.76526 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 435049.9752 | 652574.9628 | 832313.1597 | 418971.6578 | 435049.9752 | 652574.9628 | 832313.1597 | 1.05 | 1.1321 | 2.5473 | 4.1437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 1783.2715 | 713.3086 | 1069.9629 | 1369.2294 | 0.4 | 0.6 | 0.76782 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 427701.7549 | 641552.6323 | 820993.6533 | 415593.4021 | 427701.7549 | 641552.6323 | 820993.6533 | 1.05 | 1.1121 | 2.5022 | 4.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 1781.7659 | 712.7064 | 1069.0596 | 1372.4538 | 0.4 | 0.6 | 0.77028 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 420710.096 | 631065.144 | 810158.545 | 412356.6512 | 420710.096 | 631065.144 | 810158.545 | 1.05 | 1.093 | 2.4592 | 4.0531 | 1781.6583 | 712.6633 | 1068.995 | 1303.0466 | 0.4 | 0.6 | 0.73137 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 533536.4501 | 800304.6752 | 975527.7135 | 464383.4096 | 533536.4501 | 800304.6752 | 975527.7135 | 1.05 | 1.386 | 3.1185 | 4.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 1780.2588 | 712.1035 | 1068.1553 | 1375.5133 | 0.4 | 0.6 | 0.77265 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 414025.1426 | 621037.714 | 799739.1959 | 409240.5418 | 414025.1426 | 621037.714 | 799739.1959 | 1.05 | 1.0747 | 2.4181 | 4.0099 | 1780.1535 | 712.0614 | 1068.0921 | 1306.866 | 0.4 | 0.6 | 0.73413 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 524486.5653 | 786729.8479 | 962604.7282 | 460622.6873 | 524486.5653 | 786729.8479 | 962604.7282 | 1.05 | 1.3613 | 3.063 | 4.5856 | 1780.0447 | 712.0179 | 1068.0268 | 1245.6666 | 0.4 | 0.6 | 0.6998 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 638501.9931 | 957752.9896 | 1117051.4533 | 508244.3184 | 638501.9931 | 957752.9896 | 1117051.4533 | 1.05 | 1.6572 | 3.7286 | 5.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 1778.7501 | 711.5 | 1067.2501 | 1378.4263 | 0.4 | 0.6 | 0.77494 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 407612.6439 | 611418.9658 | 789689.3209 | 406231.1456 | 407612.6439 | 611418.9658 | 789689.3209 | 1.05 | 1.0572 | 2.3786 | 3.9679 | 1778.6469 | 711.4587 | 1067.1881 | 1310.4797 | 0.4 | 0.6 | 0.73678 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 515883.3048 | 773824.9572 | 950237.2344 | 457022.6602 | 515883.3048 | 773824.9572 | 950237.2344 | 1.05 | 1.3379 | 3.0102 | 4.5392 | 1778.5406 | 711.4162 | 1067.1244 | 1249.9724 | 0.4 | 0.6 | 0.70281 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 627304.0414 | 940956.0621 | 1102185.6299 | 503980.8239 | 627304.0414 | 940956.0621 | 1102185.6299 | 1.05 | 1.6267 | 3.6602 | 5.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | 1777.2399 | 710.8959 | 1066.3439 | 1381.206 | 0.4 | 0.6 | 0.77716 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 401446.869 | 602170.3035 | 779974.672 | 403318.2509 | 0.40186 | 602170.3035 | 779974.672 | 1.05 | 1.05 | 2.3406 | 3.9269 | 1777.1386 | 710.8554 | 1066.2832 | 1313.9164 | 0.4 | 0.6 | 0.73934 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 507665.4527 | 761498.1791 | 938348.2659 | 453560.2827 | 507665.4527 | 761498.1791 | 938348.2659 | 1.05 | 1.3155 | 2.9598 | 4.4941 | 1777.0346 | 710.8138 | 1066.2208 | 1254.0316 | 0.4 | 0.6 | 0.70569 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 616717.8179 | 925076.7269 | 1088025.5427 | 499921.9059 | 616717.8179 | 925076.7269 | 1088025.5427 | 1.05 | 1.5979 | 3.5953 | 4.9735 | 1776.9276 | 710.771 | 1066.1565 | 1200.0525 | 0.4 | 0.6 | 0.67535 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 728952.9316 | 1093429.3973 | 1230750.4677 | 543527.7763 | 728952.9316 | 1093429.3973 | 1230750.4677 | 1.05 | 1.8886 | 4.2494 | 5.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
390 | 1775.7281 | 710.2913 | 1065.4369 | 1383.863 | 0.4 | 0.6 | 0.77932 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 395507.1681 | 593260.7521 | 770568.0438 | 400493.8044 | 0.40504 | 593260.7521 | 770568.0438 | 1.05 | 1.05 | 2.304 | 3.887 | 1775.6287 | 710.2515 | 1065.3772 | 1317.1956 | 0.4 | 0.6 | 0.74182 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 499790.1187 | 749685.178 | 926884.8875 | 450219.8248 | 499790.1187 | 749685.178 | 926884.8875 | 1.05 | 1.2939 | 2.9114 | 4.4503 | 1775.5268 | 710.2107 | 1065.3161 | 1257.8847 | 0.4 | 0.6 | 0.70846 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 606646.0926 | 909969.1389 | 1074456.9591 | 496033.4292 | 606646.0926 | 909969.1389 | 1074456.9591 | 1.05 | 1.5705 | 3.5336 | 4.9266 | 1775.4222 | 710.1689 | 1065.2533 | 1204.4737 | 0.4 | 0.6 | 0.67842 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 716345.3876 | 1074518.0815 | 1214949.2924 | 539035.3826 | 716345.3876 | 1074518.0815 | 1214949.2924 | 1.05 | 1.8544 | 4.1724 | 5.3342 | 1775.3145 | 710.1258 | 1065.1887 | 1155.7961 | 0.4 | 0.6 | 0.65104 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 829232.9148 | 1243849.3723 | 1349654.0442 | 579972.5978 | 829232.9148 | 1243849.3723 | 1349654.0442 | 1.05 | 2.1465 | 4.8296 | 5.6862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
400 | 1774.2149 | 709.686 | 1064.529 | 1386.406 | 0.4 | 0.6 | 0.78142 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 389776.2226 | 584664.3339 | 761446.755 | 397751.1273 | 0.40818 | 584664.3339 | 761446.755 | 1.05 | 1.05 | 2.2687 | 3.8481 | 1774.1172 | 709.6469 | 1064.4703 | 1320.3318 | 0.4 | 0.6 | 0.74422 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 492224.6529 | 738336.9794 | 915807.3832 | 446989.5647 | 492224.6529 | 738336.9794 | 915807.3832 | 1.05 | 1.2733 | 2.8649 | 4.4076 | 1774.0173 | 709.6069 | 1064.4104 | 1261.5581 | 0.4 | 0.6 | 0.71113 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 597023.9043 | 895535.8565 | 1061405.0307 | 492293.1533 | 597023.9043 | 895535.8565 | 1061405.0307 | 1.05 | 1.5443 | 3.4746 | 4.8809 | 1773.9149 | 709.566 | 1064.3489 | 1208.6624 | 0.4 | 0.6 | 0.68135 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 704392.4696 | 1056588.7043 | 1199849.9356 | 534746.3414 | 704392.4696 | 1056588.7043 | 1199849.9356 | 1.05 | 1.8219 | 4.0993 | 5.2862 | 1773.8098 | 709.5239 | 1064.2859 | 1160.5166 | 0.4 | 0.6 | 0.65425 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 814593.7495 | 1221890.6242 | 1332371.6655 | 575074.1861 | 814593.7495 | 1221890.6242 | 1332371.6655 | 1.05 | 2.1068 | 4.7403 | 5.6363 | 1773.7017 | 709.4807 | 1064.221 | 1116.1573 | 0.4 | 0.6 | 0.62928 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 927961.5693 | 1391942.354 | 1459872.2318 | 613806.6245 | 927961.5693 | 1391942.354 | 1459872.2318 | 1.05 | 2.3999 | 5.3997 | 5.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
410 | 1772.3961 | 708.9584 | 1063.4377 | 1388.604 | 0.4 | 0.6 | 0.78346 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 384173.1856 | 576259.7784 | 752462.2043 | 395084.499 | 0.41136 | 576259.7784 | 752462.2043 | 1.05 | 1.05 | 2.2338 | 3.8087 | 1772.3001 | 708.92 | 1063.3801 | 1323.1093 | 0.4 | 0.6 | 0.74655 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 484859.4724 | 727289.2086 | 904928.6884 | 443860.1653 | 484859.4724 | 727289.2086 | 904928.6884 | 1.05 | 1.2529 | 2.8191 | 4.3644 | 1772.202 | 708.8808 | 1063.3212 | 1264.8533 | 0.4 | 0.6 | 0.71372 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 587702.9019 | 881554.3529 | 1048636.0083 | 488685.1722 | 587702.9019 | 881554.3529 | 1048636.0083 | 1.05 | 1.5186 | 3.4169 | 4.8348 | 1772.1017 | 708.8407 | 1063.261 | 1212.4432 | 0.4 | 0.6 | 0.68418 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 692885.0841 | 1039327.6261 | 1185151.7657 | 530631.6394 | 692885.0841 | 1039327.6261 | 1185151.7657 | 1.05 | 1.7903 | 4.0282 | 5.2378 | 1771.999 | 708.7996 | 1063.1994 | 1164.781 | 0.4 | 0.6 | 0.65733 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 800616.6544 | 1200924.9816 | 1315665.3836 | 570410.4022 | 800616.6544 | 1200924.9816 | 1315665.3836 | 1.05 | 2.0685 | 4.6542 | 5.5861 | 1771.8935 | 708.7574 | 1063.1361 | 1120.9438 | 0.4 | 0.6 | 0.63262 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 911150.7411 | 1366726.1117 | 1441041.324 | 608531.6408 | 911150.7411 | 1366726.1117 | 1441041.324 | 1.05 | 2.354 | 5.2965 | 5.8881 | 1771.7851 | 708.714 | 1063.0711 | 1080.0552 | 0.4 | 0.6 | 0.60959 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1024804.2474 | 1537206.371 | 1561765.5763 | 645389.3502 | 1024804.2474 | 1537206.371 | 1561765.5763 | 1.05 | 2.6474 | 5.9568 | 6.1486 | 1771.6733 | 708.6693 | 1041.0442 | 1041.0442 | 0.4 | 0.58761 | 0.58761 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1141990.7 | 1677598.7478 | 1677598.7478 | 681312.4479 | 1141990.7 | 1677598.7478 | 1677598.7478 | 1.05 | 2.95 | 6.3661 | 6.3661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420 | 1770.5753 | 708.2301 | 1062.3452 | 1390.7004 | 0.4 | 0.6 | 0.78545 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 378752.468 | 568128.7019 | 743728.8905 | 392488.9196 | 0.41451 | 568128.7019 | 743728.8905 | 1.05 | 1.05 | 2.2 | 3.7702 | 1770.4809 | 708.1923 | 1062.2885 | 1325.7629 | 0.4 | 0.6 | 0.74882 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 477757.671 | 716636.5065 | 894380.4579 | 440823.8436 | 477757.671 | 716636.5065 | 894380.4579 | 1.05 | 1.2333 | 2.775 | 4.3222 | 1770.3846 | 708.1538 | 1062.2307 | 1267.9995 | 0.4 | 0.6 | 0.71623 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 578749.3073 | 868123.9609 | 1036291.596 | 485197.2114 | 578749.3073 | 868123.9609 | 1036291.596 | 1.05 | 1.4939 | 3.3614 | 4.7898 | 1770.2862 | 708.1145 | 1062.1717 | 1216.0446 | 0.4 | 0.6 | 0.68692 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 681881.0868 | 1022821.6302 | 1170994.0368 | 526671.0422 | 681881.0868 | 1022821.6302 | 1170994.0368 | 1.05 | 1.7601 | 3.9601 | 5.1906 | 1770.1856 | 708.0743 | 1062.1114 | 1168.8254 | 0.4 | 0.6 | 0.66028 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 787326.7556 | 1180990.1335 | 1299648.287 | 565945.9545 | 787326.7556 | 1180990.1335 | 1299648.287 | 1.05 | 2.0321 | 4.5723 | 5.5372 | 1770.0827 | 708.0331 | 1062.0496 | 1125.4496 | 0.4 | 0.6 | 0.63582 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 895287.5299 | 1342931.2949 | 1423098.8264 | 603519.5675 | 895287.5299 | 1342931.2949 | 1423098.8264 | 1.05 | 2.3106 | 5.1989 | 5.8382 | 1769.977 | 707.9908 | 1061.9862 | 1085.0938 | 0.4 | 0.6 | 0.61306 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1006003.4854 | 1509005.2281 | 1541839.4696 | 639768.4045 | 1006003.4854 | 1509005.2281 | 1541839.4696 | 1.05 | 2.5962 | 5.8415 | 6.0985 | 1769.8685 | 707.9474 | 1046.814 | 1046.814 | 0.4 | 0.59146 | 0.59146 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1119770.6774 | 1655760.9783 | 1655760.9783 | 674995.5478 | 1119770.6774 | 1655760.9783 | 1655760.9783 | 1.05 | 2.8897 | 6.318 | 6.318 | 1769.7567 | 707.9027 | 1008.923 | 1008.923 | 0.4 | 0.57009 | 0.57009 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1236966.4081 | 1762959.6964 | 1762959.6964 | 709461.8337 | 1236966.4081 | 1762959.6964 | 1762959.6964 | 1.05 | 3.1919 | 6.4836 | 6.4836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
430 | 1768.7524 | 707.5009 | 1061.2514 | 1392.7007 | 0.4 | 0.6 | 0.78739 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 373502.3585 | 560253.5377 | 735231.5354 | 389959.9617 | 0.41763 | 560253.5377 | 735231.5354 | 1.05 | 1.05 | 2.1673 | 3.7325 | 1768.6595 | 707.4638 | 1061.1957 | 1328.3008 | 0.4 | 0.6 | 0.75102 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 470899.974 | 706349.9611 | 884139.64 | 437873.92 | 470899.974 | 706349.9611 | 884139.64 | 1.05 | 1.2144 | 2.7323 | 4.2809 | 1768.5649 | 707.426 | 1061.1389 | 1271.0085 | 0.4 | 0.6 | 0.71867 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 570132.2371 | 855198.3557 | 1024337.4629 | 481819.2671 | 570132.2371 | 855198.3557 | 1024337.4629 | 1.05 | 1.4702 | 3.3079 | 4.7458 | 1768.4684 | 707.3873 | 1061.081 | 1219.4837 | 0.4 | 0.6 | 0.68957 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 671330.7933 | 1006996.1899 | 1157324.8178 | 522849.2599 | 671330.7933 | 1006996.1899 | 1157324.8178 | 1.05 | 1.731 | 3.8949 | 5.1445 | 1768.3698 | 707.3479 | 1061.0219 | 1172.6758 | 0.4 | 0.6 | 0.66314 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 774641.8992 | 1161962.8488 | 1284239.0396 | 561656.5196 | 774641.8992 | 1161962.8488 | 1284239.0396 | 1.05 | 1.9973 | 4.494 | 5.4896 | 1768.2691 | 707.3076 | 1060.9615 | 1129.7182 | 0.4 | 0.6 | 0.63888 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 880230.731 | 1320346.0965 | 1405912.5041 | 598729.8961 | 880230.731 | 1320346.0965 | 1405912.5041 | 1.05 | 2.2694 | 5.1063 | 5.7895 | 1768.166 | 707.2664 | 1060.8996 | 1089.8273 | 0.4 | 0.6 | 0.61636 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 988287.7652 | 1482431.6477 | 1522853.2864 | 634434.8769 | 988287.7652 | 1482431.6477 | 1522853.2864 | 1.05 | 2.5479 | 5.7328 | 6.0497 | 1768.0604 | 707.2241 | 1052.1502 | 1052.1502 | 0.4 | 0.59509 | 0.59509 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1099038.1016 | 1635059.004 | 1635059.004 | 669059.4231 | 1099038.1016 | 1635059.004 | 1635059.004 | 1.05 | 2.8333 | 6.2709 | 6.2709 | 1767.9519 | 707.1807 | 1015.3279 | 1015.3279 | 0.4 | 0.5743 | 0.5743 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1212754.8792 | 1741201.1337 | 1741201.1337 | 702842.7345 | 1212754.8792 | 1741201.1337 | 1741201.1337 | 1.05 | 3.1262 | 6.4442 | 6.4442 | 1767.8402 | 707.1361 | 974.3919 | 974.3919 | 0.4 | 0.55118 | 0.55118 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1329778.3084 | 1832356.2361 | 1832356.2361 | 735995.2034 | 1329778.3084 | 1832356.2361 | 1832356.2361 | 1.05 | 3.4277 | 6.5082 | 6.5082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
440 | 1766.9274 | 706.771 | 1060.1565 | 1394.6104 | 0.4 | 0.6 | 0.78929 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 368412.3777 | 552618.5665 | 726956.4608 | 387493.6703 | 0.42072 | 552618.5665 | 726956.4608 | 1.05 | 1.05 | 2.1356 | 3.6955 | 1766.836 | 706.7344 | 1060.1016 | 1330.7301 | 0.4 | 0.6 | 0.75317 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 464269.4769 | 696404.2154 | 874186.0317 | 435004.5551 | 464269.4769 | 696404.2154 | 874186.0317 | 1.05 | 1.196 | 2.6911 | 4.2404 | 1766.743 | 706.6972 | 1060.0458 | 1273.8899 | 0.4 | 0.6 | 0.72104 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 561825.4201 | 842738.1301 | 1012744.5062 | 478542.8859 | 561825.4201 | 842738.1301 | 1012744.5062 | 1.05 | 1.4473 | 3.2564 | 4.7027 | 1766.6482 | 706.6593 | 1059.9889 | 1222.7738 | 0.4 | 0.6 | 0.69214 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 661193.8672 | 991790.8009 | 1144102.292 | 519154.0275 | 661193.8672 | 991790.8009 | 1144102.292 | 1.05 | 1.7032 | 3.8321 | 5.0995 | 1766.5516 | 706.6206 | 1059.931 | 1176.3517 | 0.4 | 0.6 | 0.6659 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 762499.5949 | 1143749.3923 | 1269376.6263 | 557523.9189 | 762499.5949 | 1143749.3923 | 1269376.6263 | 1.05 | 1.964 | 4.419 | 5.4431 | 1766.453 | 706.5812 | 1059.8718 | 1133.7788 | 0.4 | 0.6 | 0.64184 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 865881.1198 | 1298821.6797 | 1389391.158 | 594134.7475 | 865881.1198 | 1298821.6797 | 1389391.158 | 1.05 | 2.2302 | 5.0179 | 5.7421 | 1766.3523 | 706.5409 | 1059.8114 | 1094.3038 | 0.4 | 0.6 | 0.61953 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 971494.4511 | 1457241.6767 | 1504668.7943 | 629344.39 | 971494.4511 | 1457241.6767 | 1504668.7943 | 1.05 | 2.502 | 5.6296 | 6.002 | 1766.2492 | 706.4997 | 1057.1421 | 1057.1421 | 0.4 | 0.59852 | 0.59852 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1079518.4089 | 1615293.4662 | 1615293.4662 | 663431.2124 | 1079518.4089 | 1615293.4662 | 1615293.4662 | 1.05 | 2.7801 | 6.2244 | 6.2244 | 1766.1436 | 706.4574 | 1021.1553 | 1021.1553 | 0.4 | 0.57818 | 0.57818 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1190162.0804 | 1720330.6105 | 1720330.6105 | 696621.5547 | 1190162.0804 | 1720330.6105 | 1720330.6105 | 1.05 | 3.0648 | 6.4035 | 6.4035 | 1766.0353 | 706.4141 | 983.1307 | 983.1307 | 0.4 | 0.55669 | 0.55669 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1303675.1473 | 1814350.8517 | 1814350.8517 | 729108.004 | 1303675.1473 | 1814350.8517 | 1814350.8517 | 1.05 | 3.3569 | 6.502 | 6.502 | 1765.9239 | 706.3696 | 848.9653 | 848.9653 | 0.4 | 0.48075 | 0.48075 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1420362.0301 | 1707092.2748 | 1707092.2748 | 761062.6233 | 1420362.0301 | 1707092.2748 | 1707092.2748 | 1.05 | 3.6572 | 5.2828 | 5.2828 | 1765.8091 | 706.3237 | 843.6528 | 843.6528 | 0.4 | 0.47777 | 0.47777 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1540601.1205 | 1840137.1407 | 1840137.1407 | 792647.4833 | 1540601.1205 | 1840137.1407 | 1840137.1407 | 1.05 | 3.9665 | 5.6589 | 5.6589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450 | 1765.1004 | 706.0402 | 1059.0603 | 1396.434 | 0.4 | 0.6 | 0.79114 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 363473.0918 | 545209.6377 | 718891.3447 | 385086.4904 | 0.42379 | 545209.6377 | 718891.3447 | 1.05 | 1.05 | 2.1047 | 3.6593 | 1765.0105 | 706.0042 | 1059.0063 | 1333.0572 | 0.4 | 0.6 | 0.75527 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 457851.1943 | 686776.7914 | 864501.7201 | 432210.5828 | 457851.1943 | 686776.7914 | 864501.7201 | 1.05 | 1.1783 | 2.6511 | 4.2008 | 1764.919 | 705.9676 | 1058.9514 | 1276.6522 | 0.4 | 0.6 | 0.72335 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 553806.0529 | 830709.0793 | 1001487.4964 | 475360.7579 | 553806.0529 | 830709.0793 | 1001487.4964 | 1.05 | 1.4251 | 3.2066 | 4.6605 | 1764.8258 | 705.9303 | 1058.8955 | 1225.9262 | 0.4 | 0.6 | 0.69464 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 651436.37 | 977154.5549 | 1131291.419 | 515575.0994 | 651436.37 | 977154.5549 | 1131291.419 | 1.05 | 1.6763 | 3.7717 | 5.0554 | 1764.731 | 705.8924 | 1058.8386 | 1179.8684 | 0.4 | 0.6 | 0.66858 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 750849.5726 | 1126274.3589 | 1255012.3779 | 553533.7028 | 750849.5726 | 1126274.3589 | 1255012.3779 | 1.05 | 1.932 | 4.347 | 5.3976 | 1764.6344 | 705.8538 | 1058.7806 | 1137.6532 | 0.4 | 0.6 | 0.6447 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 852163.4891 | 1278245.2337 | 1373466.5986 | 589713.3408 | 852163.4891 | 1278245.2337 | 1373466.5986 | 1.05 | 2.1926 | 4.9333 | 5.6957 | 1764.5358 | 705.8143 | 1058.7215 | 1098.5563 | 0.4 | 0.6 | 0.62258 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 955508.6634 | 1433262.9951 | 1487190.1131 | 624466.2015 | 955508.6634 | 1433262.9951 | 1487190.1131 | 1.05 | 2.4583 | 5.5312 | 5.9553 | 1764.4351 | 705.7741 | 1058.6611 | 1061.8464 | 0.4 | 0.6 | 0.60181 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1061031.5366 | 1591547.3049 | 1596335.9964 | 658064.0394 | 1061031.5366 | 1591547.3049 | 1596335.9964 | 1.05 | 2.7297 | 6.1417 | 6.1788 | 1764.3322 | 705.7329 | 1026.5417 | 1026.5417 | 0.4 | 0.58183 | 0.58183 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1168898.7894 | 1700251.5069 | 1700251.5069 | 690724.9351 | 1168898.7894 | 1700251.5069 | 1700251.5069 | 1.05 | 3.007 | 6.3622 | 6.3622 | 1764.2269 | 705.6907 | 990.3383 | 990.3383 | 0.4 | 0.56134 | 0.56134 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1279303.2145 | 1795323.1584 | 1795323.1584 | 722630.6746 | 1279303.2145 | 1795323.1584 | 1795323.1584 | 1.05 | 3.2908 | 6.481 | 6.481 | 1764.1188 | 705.6475 | 849.1496 | 849.1496 | 0.4 | 0.48134 | 0.48134 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1392471.5817 | 1675647.7735 | 1675647.7735 | 753938.831 | 1392471.5817 | 1675647.7735 | 1675647.7735 | 1.05 | 3.5817 | 5.1866 | 5.1866 | 1764.0079 | 705.6032 | 844.1961 | 844.1961 | 0.4 | 0.47857 | 0.47857 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1508675.0762 | 1805005.5816 | 1805005.5816 | 784791.7933 | 1508675.0762 | 1805005.5816 | 1805005.5816 | 1.05 | 3.8804 | 5.5544 | 5.5544 | 1763.8938 | 705.5575 | 838.2633 | 838.2633 | 0.4 | 0.47523 | 0.47523 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1628243.0849 | 1934493.5909 | 1934493.5909 | 815324.0775 | 1628243.0849 | 1934493.5909 | 1934493.5909 | 1.05 | 4.1876 | 5.911 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
460 | 1763.2714 | 705.3086 | 1057.9628 | 1398.1758 | 0.4 | 0.6 | 0.79294 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 358675.9673 | 538013.9509 | 711025.0307 | 382735.21 | 0.42683 | 538013.9509 | 711025.0307 | 1.05 | 1.05 | 2.0748 | 3.6238 | 1763.1828 | 705.2731 | 1057.9097 | 1335.2878 | 0.4 | 0.6 | 0.75732 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 451631.7411 | 677447.6117 | 855070.6946 | 429487.3942 | 451631.7411 | 677447.6117 | 855070.6946 | 1.05 | 1.1611 | 2.6124 | 4.1619 | 1763.0927 | 705.2371 | 1057.8556 | 1279.3029 | 0.4 | 0.6 | 0.7256 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 546054.0805 | 819081.1208 | 990544.2429 | 472266.4672 | 546054.0805 | 819081.1208 | 990544.2429 | 1.05 | 1.4037 | 3.1584 | 4.6192 | 1763.0012 | 705.2005 | 1057.8007 | 1228.9507 | 0.4 | 0.6 | 0.69708 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 642029.0802 | 963043.6203 | 1118862.0722 | 512103.6888 | 642029.0802 | 963043.6203 | 1118862.0722 | 1.05 | 1.6504 | 3.7133 | 5.0122 | 1762.9081 | 705.1632 | 1057.7449 | 1183.2385 | 0.4 | 0.6 | 0.67119 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 739649.8378 | 1109474.7567 | 1241105.8025 | 549673.8867 | 739649.8378 | 1109474.7567 | 1241105.8025 | 1.05 | 1.9012 | 4.2777 | 5.353 | 1762.8133 | 705.1253 | 1057.688 | 1141.3585 | 0.4 | 0.6 | 0.64746 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 839017.5713 | 1258526.3569 | 1358084.6036 | 585449.2114 | 839017.5713 | 1258526.3569 | 1358084.6036 | 1.05 | 2.1565 | 4.8522 | 5.6502 | 1762.7168 | 705.0867 | 1057.6301 | 1102.6094 | 0.4 | 0.6 | 0.62552 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 940243.1124 | 1410364.6686 | 1470345.2317 | 619777.3101 | 940243.1124 | 1410364.6686 | 1470345.2317 | 1.05 | 2.4166 | 5.4373 | 5.9096 | 1762.6183 | 705.0473 | 1057.571 | 1066.3027 | 0.4 | 0.6 | 0.60495 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1043448.8994 | 1565173.3491 | 1578095.976 | 652925.0259 | 1043448.8994 | 1565173.3491 | 1578095.976 | 1.05 | 2.6817 | 6.0338 | 6.1338 | 1762.5178 | 705.0071 | 1031.5721 | 1031.5721 | 0.4 | 0.58528 | 0.58528 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1148771.6245 | 1680891.8916 | 1680891.8916 | 685104.7094 | 1148771.6245 | 1680891.8916 | 1680891.8916 | 1.05 | 2.9522 | 6.3206 | 6.3206 | 1762.4151 | 704.9661 | 996.6573 | 996.6573 | 0.4 | 0.56551 | 0.56551 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1256365.731 | 1776207.6918 | 1776207.6918 | 716491.09 | 1256365.731 | 1776207.6918 | 1776207.6918 | 1.05 | 3.2285 | 6.4529 | 6.4529 | 1762.3101 | 704.9241 | 849.2295 | 849.2295 | 0.4 | 0.48188 | 0.48188 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1366407.9974 | 1646126.1537 | 1646126.1537 | 747232.7374 | 1366407.9974 | 1646126.1537 | 1646126.1537 | 1.05 | 3.5111 | 5.0957 | 5.0957 | 1762.2026 | 704.881 | 844.5801 | 844.5801 | 0.4 | 0.47928 | 0.47928 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1479103.4976 | 1772244.2337 | 1772244.2337 | 777460.3145 | 1479103.4976 | 1772244.2337 | 1772244.2337 | 1.05 | 3.8004 | 5.4561 | 5.4561 | 1762.0922 | 704.8369 | 839.0662 | 839.0662 | 0.4 | 0.47618 | 0.47618 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1594693.2942 | 1898387.1656 | 1898387.1656 | 807292.8928 | 1594693.2942 | 1898387.1656 | 1898387.1656 | 1.05 | 4.0971 | 5.8063 | 5.8063 | 1761.9788 | 704.7915 | 832.4479 | 832.4479 | 0.4 | 0.47245 | 0.47245 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1713464.3327 | 2023817.8862 | 2023817.8862 | 836843.1272 | 1713464.3327 | 2023817.8862 | 2023817.8862 | 1.05 | 4.402 | 6.1411 | 6.1411 | 1761.862 | 704.7448 | 824.4619 | 824.4619 | 0.4 | 0.46795 | 0.46795 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1835762.2361 | 2147608.6248 | 2147608.6248 | 866221.8359 | 1835762.2361 | 2147608.6248 | 2147608.6248 | 1.05 | 4.7159 | 6.4542 | 6.4542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
470 | 1761.4404 | 704.5761 | 1056.8642 | 1399.8396 | 0.4 | 0.6 | 0.79471 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 354013.2526 | 531019.8789 | 703347.3755 | 380436.9146 | 0.42986 | 531019.8789 | 703347.3755 | 1.05 | 1.05 | 2.0457 | 3.5889 | 1761.353 | 704.5412 | 1056.8118 | 1337.4271 | 0.4 | 0.6 | 0.75932 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 445599.0922 | 668398.6383 | 845878.5581 | 426830.853 | 445599.0922 | 668398.6383 | 845878.5581 | 1.05 | 1.1444 | 2.5748 | 4.1238 | 1761.2644 | 704.5058 | 1056.7586 | 1281.8485 | 0.4 | 0.6 | 0.7278 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 538551.7043 | 807827.5564 | 979895.0377 | 469254.3263 | 538551.7043 | 807827.5564 | 979895.0377 | 1.05 | 1.383 | 3.1118 | 4.5786 | 1761.1744 | 704.4698 | 1056.7046 | 1231.8556 | 0.4 | 0.6 | 0.69945 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 632946.4586 | 949419.688 | 1106787.9173 | 508732.1318 | 632946.4586 | 949419.688 | 1106787.9173 | 1.05 | 1.6253 | 3.657 | 4.9698 | 1761.0829 | 704.4332 | 1056.6497 | 1186.4728 | 0.4 | 0.6 | 0.67372 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 728864.4372 | 1093296.6558 | 1227622.272 | 545934.2501 | 728864.4372 | 1093296.6558 | 1227622.272 | 1.05 | 1.8716 | 4.211 | 5.3093 | 1760.9899 | 704.396 | 1056.5939 | 1144.9087 | 0.4 | 0.6 | 0.65015 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 826393.2067 | 1239589.8101 | 1343200.1815 | 581328.7487 | 826393.2067 | 1239589.8101 | 1343200.1815 | 1.05 | 2.1219 | 4.7742 | 5.6057 | 1760.8952 | 704.3581 | 1056.5371 | 1106.4822 | 0.4 | 0.6 | 0.62836 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 925627.8213 | 1388441.732 | 1454076.6973 | 615259.4665 | 925627.8213 | 1388441.732 | 1454076.6973 | 1.05 | 2.3765 | 5.3472 | 5.8647 | 1760.7988 | 704.3195 | 1056.4793 | 1070.54 | 0.4 | 0.6 | 0.60799 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1026672.1235 | 1540008.1853 | 1560504.1874 | 647989.3644 | 1026672.1235 | 1540008.1853 | 1560504.1874 | 1.05 | 2.6358 | 5.9306 | 6.0895 | 1760.7006 | 704.2802 | 1036.3038 | 1036.3038 | 0.4 | 0.58857 | 0.58857 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1129640.4301 | 1662194.4474 | 1662194.4474 | 679726.5328 | 1129640.4301 | 1662194.4474 | 1662194.4474 | 1.05 | 2.9 | 6.2789 | 6.2789 | 1760.6004 | 704.2401 | 1002.367 | 1002.367 | 0.4 | 0.56933 | 0.56933 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1234659.7075 | 1757329.7699 | 1757329.7699 | 710640.7483 | 1234659.7075 | 1757329.7699 | 1757329.7699 | 1.05 | 3.1694 | 6.4209 | 6.4209 | 1760.498 | 704.1992 | 962.0681 | 962.0681 | 0.4 | 0.54647 | 0.54647 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1341872.3657 | 1833249.0939 | 1833249.0939 | 740874.5788 | 1341872.3657 | 1833249.0939 | 1833249.0939 | 1.05 | 3.4445 | 6.429 | 6.429 | 1760.3935 | 704.1574 | 844.8373 | 844.8373 | 0.4 | 0.47991 | 0.47991 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1451439.8219 | 1741415.3077 | 1741415.3077 | 770551.2076 | 1451439.8219 | 1741415.3077 | 1741415.3077 | 1.05 | 3.7255 | 5.3628 | 5.3628 | 1760.2864 | 704.1146 | 839.6799 | 839.6799 | 0.4 | 0.47701 | 0.47701 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1563547.0164 | 1864581.4419 | 1864581.4419 | 799780.225 | 1563547.0164 | 1864581.4419 | 1864581.4419 | 1.05 | 4.013 | 5.707 | 5.707 | 1760.1768 | 704.0707 | 833.5425 | 833.5425 | 0.4 | 0.47356 | 0.47356 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1678408.1003 | 1987051.1933 | 1987051.1933 | 828662.1458 | 1678408.1003 | 1987051.1933 | 1987051.1933 | 1.05 | 4.3075 | 6.0374 | 6.0374 | 1760.0642 | 704.0257 | 826.1915 | 826.1915 | 0.4 | 0.46941 | 0.46941 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1796273.5773 | 2107971.3498 | 2107971.3498 | 857292.1396 | 1796273.5773 | 2107971.3498 | 2107971.3498 | 1.05 | 4.6097 | 6.3484 | 6.3484 | 1759.9485 | 703.9794 | 817.4124 | 817.4124 | 0.4 | 0.46445 | 0.46445 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1917439.3158 | 2226398.4179 | 2226398.4179 | 885763.3175 | 1917439.3158 | 2226398.4179 | 2226398.4179 | 1.05 | 4.9204 | 6.6338 | 6.6338 | 1759.8293 | 703.9317 | 807.0862 | 807.0862 | 0.4 | 0.45862 | 0.45862 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 2042258.1578 | 2341531.4369 | 2341531.4369 | 914169.8744 | 2042258.1578 | 2341531.4369 | 2341531.4369 | 1.05 | 5.2403 | 6.8887 | 6.8887
480 | 1759.6073 | 703.8429 | 1055.7644 | 1401.4291 | 0.4 | 0.6 | 0.79644 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 349477.8798 | 524216.8197 | 695849.1208 | 378188.9498 | 0.43286 | 524216.8197 | 695849.1208 | 1.05 | 1.05 | 2.0174 | 3.5547 | 1759.5212 | 703.8085 | 1055.7127 | 1339.4796 | 0.4 | 0.6 | 0.76128 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 439742.392 | 659613.5879 | 836912.3009 | 424237.2285 | 439742.392 | 659613.5879 | 836912.3009 | 1.05 | 1.1282 | 2.5383 | 4.0863 | 1759.4339 | 703.7736 | 1055.6603 | 1284.295 | 0.4 | 0.6 | 0.72995 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 531283.0216 | 796924.5323 | 969522.2542 | 466319.2575 | 531283.0216 | 796924.5323 | 969522.2542 | 1.05 | 1.3629 | 3.0666 | 4.5388 | 1759.3453 | 703.7381 | 1055.6072 | 1234.6483 | 0.4 | 0.6 | 0.70177 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 624165.9546 | 936248.9319 | 1095045.6798 | 505453.6679 | 624165.9546 | 936248.9319 | 1095045.6798 | 1.05 | 1.6011 | 3.6025 | 4.9282 | 1759.2554 | 703.7022 | 1055.5532 | 1189.5806 | 0.4 | 0.6 | 0.67618 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 718462.0917 | 1077693.1375 | 1214531.642 | 542305.9177 | 718462.0917 | 1077693.1375 | 1214531.642 | 1.05 | 1.8429 | 4.1466 | 5.2665 | 1759.164 | 703.6656 | 1055.4984 | 1148.3156 | 0.4 | 0.6 | 0.65276 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 814247.5985 | 1221371.3978 | 1328774.941 | 577340.3813 | 814247.5985 | 1221371.3978 | 1328774.941 | 1.05 | 2.0885 | 4.6992 | 5.562 | 1759.0712 | 703.6285 | 1055.4427 | 1110.1904 | 0.4 | 0.6 | 0.63112 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 911604.6022 | 1367406.9034 | 1438336.7207 | 610897.5875 | 911604.6022 | 1367406.9034 | 1438336.7207 | 1.05 | 2.3381 | 5.2608 | 5.8207 | 1758.9767 | 703.5907 | 1055.386 | 1074.5812 | 0.4 | 0.6 | 0.61091 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1010622.0722 | 1515933.1082 | 1543504.5727 | 643237.2795 | 1010622.0722 | 1515933.1082 | 1543504.5727 | 1.05 | 2.5919 | 5.8319 | 6.0459 | 1758.8806 | 703.5522 | 1040.7782 | 1040.7782 | 0.4 | 0.59173 | 0.59173 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1111396.9352 | 1644110.674 | 1644110.674 | 674564.1933 | 1111396.9352 | 1644110.674 | 1644110.674 | 1.05 | 2.8502 | 6.2374 | 6.2374 | 1758.7826 | 703.513 | 1007.6186 | 1007.6186 | 0.4 | 0.57291 | 0.57291 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1214035.4847 | 1738823.1438 | 1738823.1438 | 705044.4031 | 1214035.4847 | 1738823.1438 | 1738823.1438 | 1.05 | 3.1133 | 6.3866 | 6.3866 | 1758.6828 | 703.4731 | 971.1163 | 971.1163 | 0.4 | 0.55218 | 0.55218 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1318655.1535 | 1820350.2605 | 1820350.2605 | 734816.2036 | 1318655.1535 | 1820350.2605 | 1820350.2605 | 1.05 | 3.3814 | 6.4438 | 6.4438 | 1758.5809 | 703.4324 | 844.99 | 844.99 | 0.4 | 0.4805 | 0.4805 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1425386.7367 | 1712229.35 | 1712229.35 | 763997.6825 | 1425386.7367 | 1712229.35 | 1712229.35 | 1.05 | 3.6549 | 5.2739 | 5.2739 | 1758.4769 | 703.3907 | 840.1414 | 840.1414 | 0.4 | 0.47777 | 0.47777 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1534377.1615 | 1832685.2453 | 1832685.2453 | 792692.2169 | 1534377.1615 | 1832685.2453 | 1832685.2453 | 1.05 | 3.9341 | 5.6125 | 5.6125 | 1758.3705 | 703.3482 | 834.416 | 834.416 | 0.4 | 0.47454 | 0.47454 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1645792.9203 | 1952483.854 | 1952483.854 | 820992.635 | 1645792.9203 | 1952483.854 | 1952483.854 | 1.05 | 4.2195 | 5.9386 | 5.9386 | 1758.2616 | 703.3047 | 827.6046 | 827.6046 | 0.4 | 0.47069 | 0.47069 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1759824.3015 | 2070850.4519 | 2070850.4519 | 848984.5117 | 1759824.3015 | 2070850.4519 | 2070850.4519 | 1.05 | 4.5116 | 6.2472 | 6.2472 | 1758.15 | 703.26 | 819.5046 | 819.5046 | 0.4 | 0.46612 | 0.46612 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1876690.5925 | 2186896.2056 | 2186896.2056 | 876748.9071 | 1876690.5925 | 2186896.2056 | 2186896.2056 | 1.05 | 4.8109 | 6.5327 | 6.5327 | 1758.0355 | 703.2142 | 809.9811 | 809.9811 | 0.4 | 0.46073 | 0.46073 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1996646.4992 | 2299791.4122 | 2299791.4122 | 904364.7683 | 1996646.4992 | 2299791.4122 | 2299791.4122 | 1.05 | 5.118 | 6.7901 | 6.7901
490 | 1757.7721 | 703.1089 | 1054.6633 | 1402.9474 | 0.4 | 0.6 | 0.79814 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 345063.3823 | 517595.0735 | 688521.7875 | 375988.8898 | 0.43585 | 517595.0735 | 688521.7875 | 1.05 | 1.05 | 1.9898 | 3.5211 | 1757.6873 | 703.0749 | 1054.6124 | 1341.4496 | 0.4 | 0.6 | 0.76319 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 434051.7997 | 651077.6996 | 828160.1179 | 421703.1417 | 434051.7997 | 651077.6996 | 828160.1179 | 1.05 | 1.1124 | 2.5029 | 4.0495 | 1757.6013 | 703.0405 | 1054.5608 | 1286.6477 | 0.4 | 0.6 | 0.73205 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 524233.7478 | 786350.6217 | 959410.0409 | 463456.7024 | 524233.7478 | 786350.6217 | 959410.0409 | 1.05 | 1.3434 | 3.0228 | 4.4997 | 1757.5141 | 703.0056 | 1054.5085 | 1237.3354 | 0.4 | 0.6 | 0.70403 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 615667.5083 | 923501.2625 | 1083614.6287 | 502262.2865 | 615667.5083 | 923501.2625 | 1083614.6287 | 1.05 | 1.5777 | 3.5498 | 4.8874 | 1757.4256 | 702.9703 | 1054.4554 | 1192.57 | 0.4 | 0.6 | 0.67859 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 708415.2894 | 1062622.9342 | 1201807.3593 | 538781.0895 | 708415.2894 | 1062622.9342 | 1201807.3593 | 1.05 | 1.8153 | 4.0844 | 5.2244 | 1757.3359 | 702.9343 | 1054.4015 | 1151.5896 | 0.4 | 0.6 | 0.6553 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 802543.6277 | 1203815.4415 | 1314775.5231 | 573474.0889 | 802543.6277 | 1203815.4415 | 1314775.5231 | 1.05 | 2.0564 | 4.6268 | 5.5191 | 1757.2447 | 702.8979 | 1054.3468 | 1113.7473 | 0.4 | 0.6 | 0.6338 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 898123.8845 | 1347185.8267 | 1423084.4497 | 606678.8629 | 898123.8845 | 1347185.8267 | 1423084.4497 | 1.05 | 2.3011 | 5.1776 | 5.7774 | 1757.1521 | 702.8608 | 1054.2912 | 1078.4446 | 0.4 | 0.6 | 0.61375 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 995232.8615 | 1492849.2922 | 1527049.9118 | 638652.392 | 995232.8615 | 1492849.2922 | 1527049.9118 | 1.05 | 2.5498 | 5.7371 | 6.003 | 1757.0579 | 702.8231 | 1045.0267 | 1045.0267 | 0.4 | 0.59476 | 0.59476 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1093953.5629 | 1626597.921 | 1626597.921 | 669596.6514 | 1093953.5629 | 1626597.921 | 1626597.921 | 1.05 | 2.8026 | 6.1962 | 6.1962 | 1756.962 | 702.7848 | 1012.5056 | 1012.5056 | 0.4 | 0.57628 | 0.57628 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1194376.1403 | 1720743.6037 | 1720743.6037 | 699674.7993 | 1194376.1403 | 1720743.6037 | 1720743.6037 | 1.05 | 3.0597 | 6.3508 | 6.3508 | 1756.8645 | 702.7458 | 978.1386 | 978.1386 | 0.4 | 0.55675 | 0.55675 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1296599.0598 | 1804711.7202 | 1804711.7202 | 729021.9097 | 1296599.0598 | 1804711.7202 | 1804711.7202 | 1.05 | 3.3214 | 6.4346 | 6.4346 | 1756.7651 | 702.706 | 845.0545 | 845.0545 | 0.4 | 0.48103 | 0.48103 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1400730.5408 | 1684479.1095 | 1684479.1095 | 757752.3862 | 1400730.5408 | 1684479.1095 | 1684479.1095 | 1.05 | 3.5879 | 5.1888 | 5.1888 | 1756.6638 | 702.6655 | 840.477 | 840.477 | 0.4 | 0.47845 | 0.47845 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1506890.3219 | 1802431.7915 | 1802431.7915 | 785965.2794 | 1506890.3219 | 1802431.7915 | 1802431.7915 | 1.05 | 3.8596 | 5.522 | 5.522 | 1756.5604 | 702.6241 | 835.1097 | 835.1097 | 0.4 | 0.47542 | 0.47542 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1615211.819 | 1919773.2358 | 1919773.2358 | 813748.2437 | 1615211.819 | 1919773.2358 | 1919773.2358 | 1.05 | 4.1368 | 5.844 | 5.844 | 1756.4547 | 702.5819 | 828.7647 | 828.7647 | 0.4 | 0.47184 | 0.47184 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1725844.7486 | 2035804.246 | 2035804.246 | 841180.5904 | 1725844.7486 | 2035804.246 | 2035804.246 | 1.05 | 4.4199 | 6.1501 | 6.1501 | 1756.3467 | 702.5387 | 821.252 | 821.252 | 0.4 | 0.46759 | 0.46759 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1838958.3028 | 2149700.9983 | 2149700.9983 | 868335.7363 | 1838958.3028 | 2149700.9983 | 2149700.9983 | 1.05 | 4.7093 | 6.4353 | 6.4353 | 1756.2362 | 702.4945 | 812.4274 | 812.4274 | 0.4 | 0.4626 | 0.4626 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1954744.982 | 2260641.9333 | 2260641.9333 | 895283.2486 | 1954744.982 | 2260641.9333 | 2260641.9333 | 1.05 | 5.0055 | 6.6947 | 6.6947
500 | 1755.935 | 702.374 | 1053.561 | 1404.3974 | 0.4 | 0.6 | 0.7998 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 340763.8245 | 511145.7368 | 681357.5839 | 373834.5101 | 0.43882 | 511145.7368 | 681357.5839 | 1.05 | 1.05 | 1.963 | 3.488 | 1755.8513 | 702.3405 | 1053.5108 | 1343.3408 | 0.4 | 0.6 | 0.76507 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 428518.3614 | 642777.5421 | 819611.2561 | 419225.5209 | 428518.3614 | 642777.5421 | 819611.2561 | 1.05 | 1.0971 | 2.4684 | 4.0134 | 1755.7666 | 702.3066 | 1053.4599 | 1288.9113 | 0.4 | 0.6 | 0.7341 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 517390.9934 | 776086.4901 | 949544.0775 | 460662.5504 | 517390.9934 | 776086.4901 | 949544.0775 | 1.05 | 1.3245 | 2.9802 | 4.4612 | 1755.6807 | 702.2723 | 1053.4084 | 1239.9229 | 0.4 | 0.6 | 0.70623 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 607433.1717 | 911149.7576 | 1072476.1881 | 499152.6116 | 607433.1717 | 911149.7576 | 1072476.1881 | 1.05 | 1.555 | 3.4987 | 4.8473 | 1755.5936 | 702.2375 | 1053.3562 | 1195.4484 | 0.4 | 0.6 | 0.68094 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 698699.6408 | 1048049.4611 | 1189425.8391 | 535352.8523 | 698699.6408 | 1048049.4611 | 1189425.8391 | 1.05 | 1.7885 | 4.0241 | 5.183 | 1755.5054 | 702.2022 | 1053.3032 | 1154.7395 | 0.4 | 0.6 | 0.65778 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 791248.737 | 1186873.1055 | 1301172.5886 | 569721.0872 | 791248.737 | 1186873.1055 | 1301172.5886 | 1.05 | 2.0253 | 4.5569 | 5.4769 | 1755.4158 | 702.1663 | 1053.2495 | 1117.1642 | 0.4 | 0.6 | 0.63641 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 885142.7516 | 1327714.1274 | 1408284.3391 | 602592.2157 | 885142.7516 | 1327714.1274 | 1408284.3391 | 1.05 | 2.2655 | 5.0974 | 5.7349 | 1755.3249 | 702.13 | 1053.1949 | 1082.1459 | 0.4 | 0.6 | 0.61649 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 980448.3706 | 1470672.5559 | 1511099.4219 | 634220.7842 | 980448.3706 | 1470672.5559 | 1511099.4219 | 1.05 | 2.5093 | 5.646 | 5.9607 | 1755.2325 | 702.093 | 1049.0739 | 1049.0739 | 0.4 | 0.59768 | 0.59768 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1077237.2109 | 1609617.9011 | 1609617.9011 | 664806.4176 | 1077237.2109 | 1609617.9011 | 1609617.9011 | 1.05 | 2.7569 | 6.1552 | 6.1552 | 1755.1387 | 702.0555 | 1017.0906 | 1017.0906 | 0.4 | 0.57949 | 0.57949 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1175586.4725 | 1703110.3691 | 1703110.3691 | 694509.8826 | 1175586.4725 | 1703110.3691 | 1703110.3691 | 1.05 | 3.0084 | 6.3142 | 6.3142 | 1755.0433 | 702.0173 | 984.1641 | 984.1641 | 0.4 | 0.56076 | 0.56076 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1275579.7315 | 1788246.245 | 1788246.245 | 723463.7097 | 1275579.7315 | 1788246.245 | 1788246.245 | 1.05 | 3.2642 | 6.4152 | 6.4152 | 1754.9462 | 701.9785 | 845.0432 | 845.0432 | 0.4 | 0.48152 | 0.48152 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1377307.9018 | 1658006.1749 | 1658006.1749 | 751779.4993 | 1377307.9018 | 1658006.1749 | 1658006.1749 | 1.05 | 3.5243 | 5.1072 | 5.1072 | 1754.8473 | 701.9389 | 840.7059 | 840.7059 | 0.4 | 0.47908 | 0.47908 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1480870.3998 | 1773625.0798 | 1773625.0798 | 779553.1248 | 1480870.3998 | 1773625.0798 | 1773625.0798 | 1.05 | 3.7891 | 5.4353 | 5.4353 | 1754.7466 | 701.8986 | 835.6533 | 835.6533 | 0.4 | 0.47622 | 0.47622 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1586376.5483 | 1888678.4475 | 1888678.4475 | 806868.5618 | 1586376.5483 | 1888678.4475 | 1888678.4475 | 1.05 | 4.0588 | 5.7531 | 5.7531 | 1754.6439 | 701.8576 | 829.7163 | 829.7163 | 0.4 | 0.47287 | 0.47287 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1693947.2639 | 2002536.7862 | 2002536.7862 | 833800.7972 | 1693947.2639 | 2002536.7862 | 2002536.7862 | 1.05 | 4.3338 | 6.0566 | 6.0566 | 1754.5391 | 701.8156 | 822.7175 | 822.7175 | 0.4 | 0.46891 | 0.46891 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1803717.0747 | 2114443.6926 | 2114443.6926 | 860418.1102 | 1803717.0747 | 2114443.6926 | 2114443.6926 | 1.05 | 4.6143 | 6.3411 | 6.3411 | 1754.432 | 701.7728 | 814.5095 | 814.5095 | 0.4 | 0.46426 | 0.46426 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1915836.5255 | 2223607.1625 | 2223607.1625 | 886783.9223 | 1915836.5255 | 2223607.1625 | 2223607.1625 | 1.05 | 4.9008 | 6.6019 | 6.6019
510 | 1754.403 | 701.7612 | 1052.6418 | 1403.5224 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 336632.7016 | 504949.0524 | 673265.4033 | 371723.7652 | 0.4417 | 504949.0524 | 673265.4033 | 1.05 | 1.05 | 1.9375 | 3.4445 | 1754.3205 | 701.7282 | 1052.5923 | 1345.3924 | 0.4 | 0.6 | 0.7669 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 423208.0246 | 634812.0369 | 811398.0006 | 416801.564 | 423208.0246 | 634812.0369 | 811398.0006 | 1.05 | 1.0825 | 2.4357 | 3.9792 | 1754.2369 | 701.6948 | 1052.5422 | 1291.3164 | 0.4 | 0.6 | 0.73611 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 510832.5513 | 766248.827 | 940076.0263 | 457933.0797 | 510832.5513 | 766248.827 | 940076.0263 | 1.05 | 1.3066 | 2.9398 | 4.425 | 1754.1523 | 701.6609 | 1052.4914 | 1242.6337 | 0.4 | 0.6 | 0.7084 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 599551.8181 | 899327.7271 | 1061799.6035 | 496119.8112 | 599551.8181 | 899327.7271 | 1061799.6035 | 1.05 | 1.5334 | 3.4503 | 4.8095 | 1754.0666 | 701.6267 | 1052.44 | 1198.4322 | 0.4 | 0.6 | 0.68323 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 689414.1394 | 1034121.2091 | 1177572.2502 | 532015.04 | 689414.1394 | 1034121.2091 | 1177572.2502 | 1.05 | 1.7632 | 3.9672 | 5.1442 | 1753.9798 | 701.5919 | 1052.3879 | 1157.9762 | 0.4 | 0.6 | 0.6602 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 780470.8342 | 1170706.2512 | 1288165.7328 | 566073.6086 | 780470.8342 | 1170706.2512 | 1288165.7328 | 1.05 | 1.996 | 4.491 | 5.4373 | 1753.8917 | 701.5567 | 1052.335 | 1120.6475 | 0.4 | 0.6 | 0.63895 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 872776.4951 | 1309164.7426 | 1394149.2763 | 598627.9501 | 872776.4951 | 1309164.7426 | 1394149.2763 | 1.05 | 2.2319 | 5.0219 | 5.695 | 1753.8024 | 701.521 | 1052.2815 | 1085.8882 | 0.4 | 0.6 | 0.61916 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 966389.3103 | 1449583.9654 | 1495879.3204 | 629930.4254 | 966389.3103 | 1449583.9654 | 1495879.3204 | 1.05 | 2.4712 | 5.5602 | 5.921 | 1753.7118 | 701.4847 | 1052.2271 | 1053.1245 | 0.4 | 0.6 | 0.60051 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1061371.4487 | 1592057.1731 | 1593414.9906 | 660178.6074 | 1061371.4487 | 1592057.1731 | 1593414.9906 | 1.05 | 2.7139 | 6.1064 | 6.1168 | 1753.6198 | 701.4479 | 1021.5977 | 1021.5977 | 0.4 | 0.58257 | 0.58257 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1157789.5217 | 1686219.4379 | 1686219.4379 | 689531.2382 | 1157789.5217 | 1686219.4379 | 1686219.4379 | 1.05 | 2.9603 | 6.2793 | 6.2793 | 1753.5264 | 701.4105 | 989.7261 | 989.7261 | 0.4 | 0.56442 | 0.56442 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1255715.136 | 1771878.2654 | 1771878.2654 | 718118.7644 | 1255715.136 | 1771878.2654 | 1771878.2654 | 1.05 | 3.2105 | 6.3924 | 6.3924 | 1753.4314 | 701.3726 | 845.1139 | 845.1139 | 0.4 | 0.48198 | 0.48198 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1355225.5551 | 1632969.4389 | 1632969.4389 | 746050.5632 | 1355225.5551 | 1632969.4389 | 1632969.4389 | 1.05 | 3.4648 | 5.0305 | 5.0305 | 1753.3348 | 701.3339 | 840.9905 | 840.9905 | 0.4 | 0.47965 | 0.47965 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1456404.4895 | 1746418.2402 | 1746418.2402 | 773420.0669 | 1456404.4895 | 1746418.2402 | 1746418.2402 | 1.05 | 3.7233 | 5.3537 | 5.3537 | 1753.2366 | 701.2946 | 836.2161 | 836.2161 | 0.4 | 0.47696 | 0.47696 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1559343.038 | 1859343.7554 | 1859343.7554 | 800308.5089 | 1559343.038 | 1859343.7554 | 1859343.7554 | 1.05 | 3.9862 | 5.6675 | 5.6675 | 1753.1365 | 701.2546 | 830.638 | 830.638 | 0.4 | 0.4738 | 0.4738 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1664140.8065 | 1971179.3445 | 1971179.3445 | 826787.741 | 1664140.8065 | 1971179.3445 | 1971179.3445 | 1.05 | 4.2538 | 5.9683 | 5.9683 | 1753.0346 | 701.2138 | 824.0918 | 824.0918 | 0.4 | 0.47009 | 0.47009 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1770907.2321 | 2081234.1484 | 2081234.1484 | 852922.4119 | 1770907.2321 | 2081234.1484 | 2081234.1484 | 1.05 | 4.5265 | 6.2519 | 6.2519 | 1752.9306 | 701.1723 | 816.4305 | 816.4305 | 0.4 | 0.46575 | 0.46575 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1879763.1472 | 2188757.4897 | 2188757.4897 | 878771.7001 | 1879763.1472 | 2188757.4897 | 2188757.4897 | 1.05 | 4.8044 | 6.5138 | 6.5138
520 | 1752.8697 | 701.1479 | 1051.7218 | 1402.2957 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 332604.8114 | 498907.217 | 665209.6227 | 369654.7678 | 0.44456 | 498907.217 | 665209.6227 | 1.05 | 1.05 | 1.9127 | 3.4003 | 1752.7882 | 701.1153 | 1051.6729 | 1347.3735 | 0.4 | 0.6 | 0.7687 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 418037.6348 | 627056.4522 | 803366.9298 | 414428.7063 | 418037.6348 | 627056.4522 | 803366.9298 | 1.05 | 1.0684 | 2.4038 | 3.9456 | 1752.7058 | 701.0823 | 1051.6235 | 1293.6424 | 0.4 | 0.6 | 0.73808 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 504456.4243 | 756684.6365 | 930826.7723 | 455264.9083 | 504456.4243 | 756684.6365 | 930826.7723 | 1.05 | 1.2892 | 2.9006 | 4.3893 | 1752.6224 | 701.049 | 1051.5735 | 1245.2568 | 0.4 | 0.6 | 0.71051 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 591901.5709 | 887852.3563 | 1051380.8105 | 493159.5246 | 591901.5709 | 887852.3563 | 1051380.8105 | 1.05 | 1.5126 | 3.4033 | 4.7724 | 1752.538 | 701.0152 | 1051.5228 | 1201.319 | 0.4 | 0.6 | 0.68547 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 680415.8207 | 1020623.731 | 1166018.1148 | 528762.1253 | 680415.8207 | 1020623.731 | 1166018.1148 | 1.05 | 1.7387 | 3.912 | 5.106 | 1752.4525 | 700.981 | 1051.4715 | 1161.1057 | 0.4 | 0.6 | 0.66256 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 770044.4483 | 1155066.6725 | 1275502.4973 | 562524.7397 | 770044.4483 | 1155066.6725 | 1275502.4973 | 1.05 | 1.9676 | 4.4271 | 5.3984 | 1752.3659 | 700.9464 | 1051.4196 | 1124.0112 | 0.4 | 0.6 | 0.64142 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 860835.4599 | 1291253.1899 | 1380403.3795 | 594777.5063 | 860835.4599 | 1291253.1899 | 1380403.3795 | 1.05 | 2.1995 | 4.9488 | 5.6558 | 1752.2782 | 700.9113 | 1051.3669 | 1089.4946 | 0.4 | 0.6 | 0.62176 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 952839.8322 | 1429259.7483 | 1481091.6709 | 625770.7938 | 952839.8322 | 1429259.7483 | 1481091.6709 | 1.05 | 2.4344 | 5.4775 | 5.882 | 1752.1892 | 700.8757 | 1051.3135 | 1057.0126 | 0.4 | 0.6 | 0.60325 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1046111.7946 | 1569167.6919 | 1577674.0251 | 655700.3491 | 1046111.7946 | 1569167.6919 | 1577674.0251 | 1.05 | 2.6726 | 6.0134 | 6.0787 | 1752.0989 | 700.8396 | 1025.8838 | 1025.8838 | 0.4 | 0.58552 | 0.58552 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1140709.163 | 1669761.7144 | 1669761.7144 | 684723.1587 | 1140709.163 | 1669761.7144 | 1669761.7144 | 1.05 | 2.9141 | 6.2441 | 6.2441 | 1752.0073 | 700.8029 | 994.831 | 994.831 | 0.4 | 0.56782 | 0.56782 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1236693.7333 | 1755559.5589 | 1755559.5589 | 712967.9112 | 1236693.7333 | 1755559.5589 | 1755559.5589 | 1.05 | 3.1592 | 6.3662 | 6.3662 | 1751.9143 | 700.7657 | 958.0094 | 958.0094 | 0.4 | 0.54684 | 0.54684 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1334131.7475 | 1823877.343 | 1823877.343 | 740542.1609 | 1334131.7475 | 1823877.343 | 1823877.343 | 1.05 | 3.4079 | 6.3691 | 6.3691 | 1751.8199 | 700.7279 | 841.1961 | 841.1961 | 0.4 | 0.48018 | 0.48018 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1433094.4426 | 1720373.1018 | 1720373.1018 | 767537.3943 | 1433094.4426 | 1720373.1018 | 1720373.1018 | 1.05 | 3.6605 | 5.2752 | 5.2752 | 1751.7239 | 700.6895 | 836.6701 | 836.6701 | 0.4 | 0.47763 | 0.47763 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1533658.6979 | 1831290.851 | 1831290.851 | 794032.7181 | 1533658.6979 | 1831290.851 | 1831290.851 | 1.05 | 3.9171 | 5.5851 | 5.5851 | 1751.6263 | 700.6505 | 831.411 | 831.411 | 0.4 | 0.47465 | 0.47465 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1635907.7962 | 1941212.709 | 1941212.709 | 820097.6147 | 1635907.7962 | 1941212.709 | 1941212.709 | 1.05 | 4.1781 | 5.8831 | 5.8831 | 1751.5269 | 700.6108 | 825.2668 | 825.2668 | 0.4 | 0.47117 | 0.47117 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1739932.3164 | 2049509.5267 | 2049509.5267 | 845794.0543 | 1739932.3164 | 2049509.5267 | 2049509.5267 | 1.05 | 4.4435 | 6.1654 | 6.1654 | 1751.4258 | 700.5703 | 818.0942 | 818.0942 | 0.4 | 0.4671 | 0.4671 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1845831.1781 | 2155477.8316 | 2155477.8316 | 871178.1538 | 1845831.1781 | 2155477.8316 | 2155477.8316 | 1.05 | 4.7137 | 6.4278 | 6.4278
530 | 1751.3349 | 700.5339 | 1050.8009 | 1401.0679 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 328675.5275 | 493013.2912 | 657351.055 | 367625.7725 | 0.4474 | 493013.2912 | 657351.055 | 1.05 | 1.05 | 1.8884 | 3.3572 | 1751.2545 | 700.5018 | 1050.7527 | 1349.2871 | 0.4 | 0.6 | 0.77047 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 413000.3716 | 619500.5574 | 795509.8315 | 412104.5936 | 413000.3716 | 619500.5574 | 795509.8315 | 1.05 | 1.0546 | 2.3728 | 3.9126 | 1751.1732 | 700.4693 | 1050.7039 | 1295.8928 | 0.4 | 0.6 | 0.74001 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 498253.004 | 747379.506 | 921785.6093 | 452654.9529 | 498253.004 | 747379.506 | 921785.6093 | 1.05 | 1.2722 | 2.8624 | 4.3543 | 1751.091 | 700.4364 | 1050.6546 | 1247.7964 | 0.4 | 0.6 | 0.71258 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 584469.3277 | 876703.9915 | 1041206.1962 | 490267.8008 | 584469.3277 | 876703.9915 | 1041206.1962 | 1.05 | 1.4923 | 3.3576 | 4.7358 | 1751.0078 | 700.4031 | 1050.6047 | 1204.114 | 0.4 | 0.6 | 0.68767 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 671687.2506 | 1007530.8759 | 1154746.4813 | 525589.1316 | 671687.2506 | 1007530.8759 | 1154746.4813 | 1.05 | 1.7149 | 3.8585 | 5.0684 | 1750.9236 | 700.3694 | 1050.5542 | 1164.1344 | 0.4 | 0.6 | 0.66487 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 759946.8194 | 1139920.2292 | 1263162.1927 | 559068.295 | 759946.8194 | 1139920.2292 | 1263162.1927 | 1.05 | 1.9401 | 4.3652 | 5.3602 | 1750.8384 | 700.3354 | 1050.503 | 1127.2633 | 0.4 | 0.6 | 0.64384 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 849290.3751 | 1273935.5626 | 1367022.012 | 591033.2767 | 849290.3751 | 1273935.5626 | 1367022.012 | 1.05 | 2.1681 | 4.8782 | 5.6172 | 1750.7521 | 700.3008 | 1050.4512 | 1092.9749 | 0.4 | 0.6 | 0.62429 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 939762.7325 | 1409644.0988 | 1466708.3583 | 621732.6088 | 939762.7325 | 1409644.0988 | 1466708.3583 | 1.05 | 2.3989 | 5.3976 | 5.8435 | 1750.6646 | 700.2659 | 1050.3988 | 1060.7522 | 0.4 | 0.6 | 0.60591 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1031411.3907 | 1547117.086 | 1562366.4127 | 651360.3877 | 1031411.3907 | 1547117.086 | 1562366.4127 | 1.05 | 2.6328 | 5.9237 | 6.041 | 1750.576 | 700.2304 | 1029.975 | 1029.975 | 0.4 | 0.58836 | 0.58836 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1124286.7775 | 1653723.2637 | 1653723.2637 | 680072.0484 | 1124286.7775 | 1653723.2637 | 1653723.2637 | 1.05 | 2.8697 | 6.2088 | 6.2088 | 1750.4862 | 700.1945 | 999.582 | 999.582 | 0.4 | 0.57103 | 0.57103 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1218442.5359 | 1739421.2954 | 1739421.2954 | 707994.7625 | 1218442.5359 | 1739421.2954 | 1739421.2954 | 1.05 | 3.1098 | 6.3378 | 6.3378 | 1750.395 | 700.158 | 965.9211 | 965.9211 | 0.4 | 0.55183 | 0.55183 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1313935.8577 | 1812674.2084 | 1812674.2084 | 735234.5493 | 1313935.8577 | 1812674.2084 | 1812674.2084 | 1.05 | 3.3534 | 6.3823 | 6.3823 | 1750.3026 | 700.121 | 841.3325 | 841.3325 | 0.4 | 0.48068 | 0.48068 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1410827.8735 | 1695385.9932 | 1695385.9932 | 761881.2974 | 1410827.8735 | 1695385.9932 | 1695385.9932 | 1.05 | 3.6005 | 5.1994 | 5.1994 | 1750.2087 | 700.0835 | 837.0296 | 837.0296 | 0.4 | 0.47825 | 0.47825 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1509184.1072 | 1804401.5517 | 1804401.5517 | 788012.409 | 1509184.1072 | 1804401.5517 | 1804401.5517 | 1.05 | 3.8513 | 5.5054 | 5.5054 | 1750.1133 | 700.0453 | 832.0556 | 832.0556 | 0.4 | 0.47543 | 0.47543 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1609075.0052 | 1912504.5381 | 1912504.5381 | 813695.5125 | 1609075.0052 | 1912504.5381 | 1912504.5381 | 1.05 | 4.106 | 5.8006 | 5.8006 | 1750.0164 | 700.0066 | 826.2706 | 826.2706 | 0.4 | 0.47215 | 0.47215 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1710576.552 | 2019122.7442 | 2019122.7442 | 838990.5287 | 1710576.552 | 2019122.7442 | 2019122.7442 | 1.05 | 4.3648 | 6.0814 | 6.0814 | 1749.9179 | 699.9671 | 819.5365 | 819.5365 | 0.4 | 0.46833 | 0.46833 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1813770.9836 | 2123601.9366 | 2123601.9366 | 863951.2806 | 1813770.9836 | 2123601.9366 | 2123601.9366 | 1.05 | 4.6278 | 6.3439 | 6.3439
540 | 1749.7986 | 699.9194 | 1049.8792 | 1399.8389 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 324840.5564 | 487260.8346 | 649681.1128 | 365635.1603 | 0.45023 | 487260.8346 | 649681.1128 | 1.05 | 1.05 | 1.8647 | 3.3151 | 1749.7192 | 699.8877 | 1049.8315 | 1351.1357 | 0.4 | 0.6 | 0.7722 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 408089.9502 | 612134.9253 | 787819.1303 | 409827.0583 | 0.4017 | 612134.9253 | 787819.1303 | 1.05 | 1.05 | 2.3425 | 3.8801 | 1749.639 | 699.8556 | 1049.7834 | 1298.071 | 0.4 | 0.6 | 0.74191 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 492213.496 | 738320.2439 | 912942.7277 | 450100.3932 | 492213.496 | 738320.2439 | 912942.7277 | 1.05 | 1.2557 | 2.8253 | 4.3197 | 1749.5579 | 699.8232 | 1049.7348 | 1250.2565 | 0.4 | 0.6 | 0.71461 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 577243.1721 | 865864.7582 | 1031263.3643 | 487441.0485 | 577243.1721 | 865864.7582 | 1031263.3643 | 1.05 | 1.4725 | 3.3132 | 4.6999 | 1749.476 | 699.7904 | 1049.6856 | 1206.822 | 0.4 | 0.6 | 0.68982 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 663212.6701 | 994819.0051 | 1143741.9995 | 522491.5608 | 663212.6701 | 994819.0051 | 1143741.9995 | 1.05 | 1.6918 | 3.8064 | 5.0314 | 1749.393 | 699.7572 | 1049.6358 | 1167.0677 | 0.4 | 0.6 | 0.66713 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 750157.4988 | 1125236.2481 | 1251126.1797 | 555698.716 | 750157.4988 | 1125236.2481 | 1251126.1797 | 1.05 | 1.9134 | 4.3052 | 5.3225 | 1749.3091 | 699.7237 | 1049.5855 | 1130.4103 | 0.4 | 0.6 | 0.6462 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 838115.1043 | 1257172.6565 | 1353983.0652 | 587388.4652 | 838115.1043 | 1257172.6565 | 1353983.0652 | 1.05 | 2.1377 | 4.8098 | 5.5791 | 1749.2242 | 699.6897 | 1049.5345 | 1096.3377 | 0.4 | 0.6 | 0.62676 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 927125.0075 | 1390687.5112 | 1452704.1631 | 617807.631 | 927125.0075 | 1390687.5112 | 1452704.1631 | 1.05 | 2.3646 | 5.3204 | 5.8055 | 1749.1383 | 699.6553 | 1049.483 | 1064.3551 | 0.4 | 0.6 | 0.6085 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1017228.9617 | 1525843.4425 | 1547466.0713 | 647148.8002 | 1017228.9617 | 1525843.4425 | 1547466.0713 | 1.05 | 2.5943 | 5.8372 | 6.0038 | 1749.0512 | 699.6205 | 1033.8922 | 1033.8922 | 0.4 | 0.59112 | 0.59112 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1108471.1355 | 1638087.6911 | 1638087.6911 | 675566.0157 | 1108471.1355 | 1638087.6911 | 1638087.6911 | 1.05 | 2.8268 | 6.1735 | 6.1735 | 1748.963 | 699.5852 | 1004.0458 | 1004.0458 | 0.4 | 0.57408 | 0.57408 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1200898.3234 | 1723531.1653 | 1723531.1653 | 703185.1153 | 1200898.3234 | 1723531.1653 | 1723531.1653 | 1.05 | 3.0624 | 6.308 | 6.308 | 1748.8736 | 699.5494 | 972.2537 | 972.2537 | 0.4 | 0.55593 | 0.55593 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1294560.1895 | 1799216.6012 | 1799216.6012 | 730110.7981 | 1294560.1895 | 1799216.6012 | 1799216.6012 | 1.05 | 3.3011 | 6.3764 | 6.3764 | 1748.783 | 699.5132 | 841.4078 | 841.4078 | 0.4 | 0.48114 | 0.48114 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1389509.5486 | 1671368.2225 | 1671368.2225 | 756431.608 | 1389509.5486 | 1671368.2225 | 1671368.2225 | 1.05 | 3.543 | 5.1262 | 5.1262 | 1748.6911 | 699.4764 | 837.3063 | 837.3063 | 0.4 | 0.47882 | 0.47882 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1485802.6916 | 1778575.8326 | 1778575.8326 | 782223.5442 | 1485802.6916 | 1778575.8326 | 1778575.8326 | 1.05 | 3.7883 | 5.4284 | 5.4284 | 1748.5978 | 699.4391 | 832.5886 | 832.5886 | 0.4 | 0.47615 | 0.47615 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1583499.7601 | 1884944.3852 | 1884944.3852 | 807552.7413 | 1583499.7601 | 1884944.3852 | 1884944.3852 | 1.05 | 4.0372 | 5.7206 | 5.7206 | 1748.5031 | 699.4013 | 827.1259 | 827.1259 | 0.4 | 0.47305 | 0.47305 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1682665.1794 | 1989953.5687 | 1989953.5687 | 832477.5033 | 1682665.1794 | 1989953.5687 | 1989953.5687 | 1.05 | 4.2898 | 5.9997 | 5.9997 | 1748.407 | 699.3628 | 820.7867 | 820.7867 | 0.4 | 0.46945 | 0.46945 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1783368.1554 | 2092998.0189 | 2092998.0189 | 857049.8784 | 1783368.1554 | 2092998.0189 | 2092998.0189 | 1.05 | 4.5463 | 6.262 | 6.262
550 | 1748.2609 | 699.3044 | 1048.9565 | 1398.6087 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 321095.9035 | 481643.8552 | 642191.807 | 363681.4259 | 0.45305 | 481643.8552 | 642191.807 | 1.05 | 1.05 | 1.8416 | 3.274 | 1748.1825 | 699.273 | 1048.9095 | 1352.922 | 0.4 | 0.6 | 0.7739 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 403300.5637 | 604950.8455 | 780287.8186 | 407594.0991 | 0.40426 | 604950.8455 | 780287.8186 | 1.05 | 1.05 | 2.313 | 3.8481 | 1748.1034 | 699.2413 | 1048.862 | 1300.18 | 0.4 | 0.6 | 0.74377 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 486329.8265 | 729494.7397 | 904289.1117 | 447598.6418 | 486329.8265 | 729494.7397 | 904289.1117 | 1.05 | 1.2396 | 2.789 | 4.2857 | 1748.0234 | 699.2093 | 1048.814 | 1252.6406 | 0.4 | 0.6 | 0.7166 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 570212.2305 | 855318.3457 | 1021540.9889 | 484675.9917 | 570212.2305 | 855318.3457 | 1021540.9889 | 1.05 | 1.4533 | 3.27 | 4.6644 | 1747.9425 | 699.177 | 1048.7655 | 1209.4472 | 0.4 | 0.6 | 0.69193 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 654977.7824 | 982466.6735 | 1132990.7203 | 519465.3331 | 654977.7824 | 982466.6735 | 1132990.7203 | 1.05 | 1.6693 | 3.7559 | 4.9949 | 1747.8608 | 699.1443 | 1048.7165 | 1169.9108 | 0.4 | 0.6 | 0.66934 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 740658.0395 | 1110987.0593 | 1239377.6001 | 552410.9877 | 740658.0395 | 1110987.0593 | 1239377.6001 | 1.05 | 1.8876 | 4.247 | 5.2853 | 1747.7782 | 699.1113 | 1048.6669 | 1133.4585 | 0.4 | 0.6 | 0.64851 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 827286.203 | 1240929.3044 | 1341266.6164 | 583836.9728 | 827286.203 | 1240929.3044 | 1341266.6164 | 1.05 | 2.1082 | 4.7435 | 5.5416 | 1747.6946 | 699.0778 | 1048.6168 | 1099.5906 | 0.4 | 0.6 | 0.62917 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 914897.2233 | 1372345.835 | 1439056.369 | 613988.5071 | 914897.2233 | 1372345.835 | 1439056.369 | 1.05 | 2.3314 | 5.2456 | 5.768 | 1747.6101 | 699.044 | 1048.566 | 1067.8317 | 0.4 | 0.6 | 0.61102 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1003527.9213 | 1505291.8819 | 1532949.195 | 643056.7828 | 1003527.9213 | 1505291.8819 | 1532949.195 | 1.05 | 2.5571 | 5.7535 | 5.9669 | 1747.5245 | 699.0098 | 1037.6524 | 1037.6524 | 0.4 | 0.59378 | 0.59378 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1093217.1248 | 1622837.6367 | 1622837.6367 | 671194.5778 | 1093217.1248 | 1622837.6367 | 1622837.6367 | 1.05 | 2.7855 | 6.1382 | 6.1382 | 1747.4379 | 698.9751 | 1008.2689 | 1008.2689 | 0.4 | 0.577 | 0.577 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1184005.8272 | 1707923.765 | 1707923.765 | 698526.5397 | 1184005.8272 | 1707923.765 | 1707923.765 | 1.05 | 3.0167 | 6.2771 | 6.2771 | 1747.3501 | 698.9401 | 977.7633 | 977.7633 | 0.4 | 0.55957 | 0.55957 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1275937.3665 | 1784938.1727 | 1784938.1727 | 725156.212 | 1275937.3665 | 1784938.1727 | 1784938.1727 | 1.05 | 3.2508 | 6.3617 | 6.3617 | 1747.2613 | 698.9045 | 841.4287 | 841.4287 | 0.4 | 0.48157 | 0.48157 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1369057.6319 | 1648242.825 | 1648242.825 | 751170.9839 | 1369057.6319 | 1648242.825 | 1648242.825 | 1.05 | 3.4878 | 5.0554 | 5.0554 | 1747.1712 | 698.8685 | 837.5099 | 837.5099 | 0.4 | 0.47935 | 0.47935 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1463415.2999 | 1753727.4928 | 1753727.4928 | 776645.6737 | 1463415.2999 | 1753727.4928 | 1753727.4928 | 1.05 | 3.728 | 5.3539 | 5.3539 | 1747.0799 | 698.832 | 833.0238 | 833.0238 | 0.4 | 0.47681 | 0.47681 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1559062.1043 | 1858437.9012 | 1858437.9012 | 801645.1833 | 1559062.1043 | 1858437.9012 | 1858437.9012 | 1.05 | 3.9715 | 5.6431 | 5.6431 | 1746.9873 | 698.7949 | 827.8516 | 827.8516 | 0.4 | 0.47387 | 0.47387 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1656053.1448 | 1961900.6796 | 1961900.6796 | 826226.5071 | 1656053.1448 | 1961900.6796 | 1961900.6796 | 1.05 | 4.2183 | 5.9203 | 5.9203 | 1746.8933 | 698.7573 | 821.8691 | 821.8691 | 0.4 | 0.47047 | 0.47047 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1754447.2402 | 2063557.5158 | 2063557.5158 | 850440.2825 | 1754447.2402 | 2063557.5158 | 2063557.5158 | 1.05 | 4.4687 | 6.1821 | 6.1821
560 | 1746.7218 | 698.6887 | 1048.0331 | 1397.3774 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 317437.8437 | 476156.7655 | 634875.6874 | 361763.166 | 0.45585 | 476156.7655 | 634875.6874 | 1.05 | 1.05 | 1.819 | 3.2338 | 1746.6444 | 698.6577 | 1047.9866 | 1354.6482 | 0.4 | 0.6 | 0.77557 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 398626.8323 | 597940.2484 | 772909.3964 | 405403.8631 | 0.4068 | 597940.2484 | 772909.3964 | 1.05 | 1.05 | 2.2842 | 3.8165 | 1746.5662 | 698.6265 | 1047.9397 | 1302.2226 | 0.4 | 0.6 | 0.74559 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 480594.5617 | 720891.8426 | 895816.4509 | 445147.3181 | 480594.5617 | 720891.8426 | 895816.4509 | 1.05 | 1.2239 | 2.7537 | 4.2523 | 1746.4873 | 698.5949 | 1047.8924 | 1254.9522 | 0.4 | 0.6 | 0.71856 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 563366.5488 | 845049.8232 | 1012028.6898 | 481969.6336 | 563366.5488 | 845049.8232 | 1012028.6898 | 1.05 | 1.4346 | 3.2279 | 4.6295 | 1746.4075 | 698.563 | 1047.8445 | 1211.9936 | 0.4 | 0.6 | 0.69399 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 646969.5722 | 970454.3584 | 1122479.9251 | 516506.7356 | 646969.5722 | 970454.3584 | 1122479.9251 | 1.05 | 1.6474 | 3.7067 | 4.959 | 1746.327 | 698.5308 | 1047.7962 | 1172.6682 | 0.4 | 0.6 | 0.67151 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 731431.7383 | 1097147.6075 | 1227901.1528 | 549200.5691 | 731431.7383 | 1097147.6075 | 1227901.1528 | 1.05 | 1.8624 | 4.1904 | 5.2487 | 1746.2456 | 698.4982 | 1047.7473 | 1136.4134 | 0.4 | 0.6 | 0.65078 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 816782.5539 | 1225173.8309 | 1328854.6451 | 580373.3039 | 816782.5539 | 1225173.8309 | 1328854.6451 | 1.05 | 2.0796 | 4.6792 | 5.5046 | 1746.1633 | 698.4653 | 1047.698 | 1102.7404 | 0.4 | 0.6 | 0.63152 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 903053.0086 | 1354579.5128 | 1425744.4417 | 610268.6446 | 903053.0086 | 1354579.5128 | 1425744.4417 | 1.05 | 2.2992 | 5.1732 | 5.731 | 1746.0801 | 698.432 | 1047.648 | 1071.191 | 0.4 | 0.6 | 0.61348 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 990275.6673 | 1485413.5009 | 1518794.0406 | 639076.4834 | 990275.6673 | 1485413.5009 | 1518794.0406 | 1.05 | 2.5211 | 5.6726 | 5.9304 | 1745.9959 | 698.3984 | 1041.2698 | 1041.2698 | 0.4 | 0.59638 | 0.59638 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1078484.7754 | 1607955.6437 | 1607955.6437 | 666948.4365 | 1078484.7754 | 1607955.6437 | 1607955.6437 | 1.05 | 2.7456 | 6.1031 | 6.1031 | 1745.9108 | 698.3643 | 1012.2853 | 1012.2853 | 0.4 | 0.5798 | 0.5798 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1167716.3772 | 1692615.2494 | 1692615.2494 | 694008.0765 | 1167716.3772 | 1692615.2494 | 1692615.2494 | 1.05 | 2.9726 | 6.2456 | 6.2456 | 1745.8246 | 698.3298 | 982.7369 | 982.7369 | 0.4 | 0.56291 | 0.56291 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1258008.4509 | 1770354.3394 | 1770354.3394 | 720357.9197 | 1258008.4509 | 1770354.3394 | 1770354.3394 | 1.05 | 3.2023 | 6.3418 | 6.3418 | 1745.7374 | 698.295 | 841.4009 | 841.4009 | 0.4 | 0.48197 | 0.48197 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1349401.0615 | 1625942.3254 | 1625942.3254 | 746084.3476 | 1349401.0615 | 1625942.3254 | 1625942.3254 | 1.05 | 3.4348 | 4.9868 | 4.9868 | 1745.6491 | 698.2596 | 837.6488 | 837.6488 | 0.4 | 0.47985 | 0.47985 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1441936.5344 | 1729781.2991 | 1729781.2991 | 771261.1657 | 1441936.5344 | 1729781.2991 | 1729781.2991 | 1.05 | 3.6701 | 5.2816 | 5.2816 | 1745.5596 | 698.2238 | 833.3726 | 833.3726 | 0.4 | 0.47742 | 0.47742 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1535659.6526 | 1832903.1784 | 1832903.1784 | 795952.2372 | 1535659.6526 | 1832903.1784 | 1832903.1784 | 1.05 | 3.9085 | 5.5679 | 5.5679 | 1745.4689 | 698.1876 | 828.4632 | 828.4632 | 0.4 | 0.47464 | 0.47464 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1630617.8808 | 1934876.859 | 1934876.859 | 820213.4726 | 1630617.8808 | 1934876.859 | 1934876.859 | 1.05 | 4.1499 | 5.8431 | 5.8431 | 1745.3771 | 698.1508 | 822.8039 | 822.8039 | 0.4 | 0.47142 | 0.47142 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1726861.6186 | 2035188.4469 | 2035188.4469 | 844094.3611 | 1726861.6186 | 2035188.4469 | 2035188.4469 | 1.05 | 4.3946 | 6.104 | 6.104
570 | 1745.1812 | 698.0725 | 1047.1087 | 1396.1449 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 313862.8958 | 470794.3437 | 627725.7916 | 359879.0699 | 0.45864 | 470794.3437 | 627725.7916 | 1.05 | 1.05 | 1.797 | 3.1946 | 1745.1047 | 698.0419 | 1047.0628 | 1356.3165 | 0.4 | 0.6 | 0.77721 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 394063.7596 | 591095.6394 | 765677.8193 | 403254.6306 | 0.40933 | 591095.6394 | 765677.8193 | 1.05 | 1.05 | 2.256 | 3.7855 | 1745.0275 | 698.011 | 1047.0165 | 1304.2013 | 0.4 | 0.6 | 0.74738 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 475000.8382 | 712501.2573 | 887517.0638 | 442744.2256 | 475000.8382 | 712501.2573 | 887517.0638 | 1.05 | 1.2086 | 2.7193 | 4.2193 | 1744.9496 | 697.9799 | 1046.9698 | 1257.1942 | 0.4 | 0.6 | 0.72048 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 556696.9879 | 835045.4818 | 1002716.9248 | 479319.2241 | 556696.9879 | 835045.4818 | 1002716.9248 | 1.05 | 1.4164 | 3.1868 | 4.5951 | 1744.871 | 697.9484 | 1046.9226 | 1214.4646 | 0.4 | 0.6 | 0.69602 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 639176.153 | 958764.2294 | 1112197.9804 | 513612.3784 | 639176.153 | 958764.2294 | 1112197.9804 | 1.05 | 1.6261 | 3.6588 | 4.9236 | 1744.7916 | 697.9166 | 1046.8749 | 1175.3442 | 0.4 | 0.6 | 0.67363 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 722463.4177 | 1083695.1265 | 1216682.903 | 546063.3342 | 722463.4177 | 1083695.1265 | 1216682.903 | 1.05 | 1.838 | 4.1354 | 5.2126 | 1744.7113 | 697.8845 | 1046.8268 | 1139.2798 | 0.4 | 0.6 | 0.65299 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 806585.0641 | 1209877.5962 | 1316730.7952 | 576992.4891 | 806585.0641 | 1209877.5962 | 1316730.7952 | 1.05 | 2.0519 | 4.6167 | 5.4682 | 1744.6303 | 697.8521 | 1046.7782 | 1105.793 | 0.4 | 0.6 | 0.63383 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 891568.6365 | 1337352.9548 | 1412749.7594 | 606642.1093 | 891568.6365 | 1337352.9548 | 1412749.7594 | 1.05 | 2.268 | 5.1029 | 5.6945 | 1744.5483 | 697.8193 | 1046.729 | 1074.4408 | 0.4 | 0.6 | 0.61588 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 977443.0132 | 1466164.5197 | 1504980.7297 | 635200.8667 | 977443.0132 | 1466164.5197 | 1504980.7297 | 1.05 | 2.4863 | 5.5941 | 5.8943 | 1744.4655 | 697.7862 | 1044.7562 | 1044.7562 | 0.4 | 0.5989 | 0.5989 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1064238.487 | 1593424.6566 | 1593424.6566 | 662819.3017 | 1064238.487 | 1593424.6566 | 1593424.6566 | 1.05 | 2.7069 | 6.0682 | 6.0682 | 1744.3818 | 697.7527 | 1016.1207 | 1016.1207 | 0.4 | 0.58251 | 0.58251 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1151986.8564 | 1677611.0624 | 1677611.0624 | 689620.0044 | 1151986.8564 | 1677611.0624 | 1677611.0624 | 1.05 | 2.93 | 6.2137 | 6.2137 | 1744.2971 | 697.7188 | 987.3203 | 987.3203 | 0.4 | 0.56603 | 0.56603 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1240721.5269 | 1755706.6355 | 1755706.6355 | 715704.5675 | 1240721.5269 | 1755706.6355 | 1755706.6355 | 1.05 | 3.1555 | 6.3187 | 6.3187 | 1744.2115 | 697.6846 | 952.618 | 952.618 | 0.4 | 0.54616 | 0.54616 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1330477.6258 | 1816633.1647 | 1816633.1647 | 741158.4799 | 1330477.6258 | 1816633.1647 | 1816633.1647 | 1.05 | 3.3836 | 6.3081 | 6.3081 | 1744.1248 | 697.6499 | 837.7299 | 837.7299 | 0.4 | 0.48032 | 0.48032 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1421292.1321 | 1706670.9826 | 1706670.9826 | 766054.6647 | 1421292.1321 | 1706670.9826 | 1706670.9826 | 1.05 | 3.6144 | 5.2116 | 5.2116 | 1744.037 | 697.6148 | 833.6449 | 833.6449 | 0.4 | 0.478 | 0.478 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1513204.0212 | 1808268.2944 | 1808268.2944 | 790456.0946 | 1513204.0212 | 1808268.2944 | 1808268.2944 | 1.05 | 3.8479 | 5.4949 | 5.4949 | 1743.9482 | 697.5793 | 828.9742 | 828.9742 | 0.4 | 0.47534 | 0.47534 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1606254.4302 | 1908805.9014 | 1908805.9014 | 814417.7654 | 1606254.4302 | 1908805.9014 | 1908805.9014 | 1.05 | 4.0844 | 5.7679 | 5.7679 | 1743.8582 | 697.5433 | 823.6084 | 823.6084 | 0.4 | 0.47229 | 0.47229 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1700486.8421 | 2007811.2916 | 2007811.2916 | 837988.2129 | 1700486.8421 | 2007811.2916 | 2007811.2916 | 1.05 | 4.3237 | 6.0278 | 6.0278
580 | 1743.6392 | 697.4557 | 1046.1835 | 1394.9113 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 310367.7997 | 465551.6996 | 620735.5995 | 358027.91 | 0.46142 | 465551.6996 | 620735.5995 | 1.05 | 1.05 | 1.7754 | 3.1562 | 1743.5636 | 697.4254 | 1046.1382 | 1357.9289 | 0.4 | 0.6 | 0.77882 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 389606.6945 | 584410.0417 | 758587.4524 | 401144.8013 | 0.41185 | 584410.0417 | 758587.4524 | 1.05 | 1.05 | 2.2285 | 3.7549 | 1743.4874 | 697.395 | 1046.0924 | 1306.1184 | 0.4 | 0.6 | 0.74914 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 469542.3022 | 704313.4532 | 879383.8309 | 440387.3321 | 469542.3022 | 704313.4532 | 879383.8309 | 1.05 | 1.1936 | 2.6857 | 4.1867 | 1743.4105 | 697.3642 | 1046.0463 | 1259.3694 | 0.4 | 0.6 | 0.72236 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 550195.1324 | 825292.6986 | 993596.8971 | 476722.2323 | 550195.1324 | 825292.6986 | 993596.8971 | 1.05 | 1.3986 | 3.1468 | 4.5612 | 1743.3329 | 697.3331 | 1045.9997 | 1216.8635 | 0.4 | 0.6 | 0.69801 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 631586.6348 | 947379.9522 | 1102134.2133 | 510779.1575 | 631586.6348 | 947379.9522 | 1102134.2133 | 1.05 | 1.6054 | 3.6122 | 4.8887 | 1743.2545 | 697.3018 | 1045.9527 | 1177.9426 | 0.4 | 0.6 | 0.67571 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 713739.2407 | 1070608.861 | 1205710.1206 | 542995.5227 | 713739.2407 | 1070608.861 | 1205710.1206 | 1.05 | 1.8142 | 4.0819 | 5.1771 | 1743.1754 | 697.2702 | 1045.9052 | 1142.0622 | 0.4 | 0.6 | 0.65516 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 796676.4093 | 1195014.6139 | 1304880.1733 | 573690.0189 | 796676.4093 | 1195014.6139 | 1304880.1733 | 1.05 | 2.0249 | 4.556 | 5.4322 | 1743.0955 | 697.2382 | 1045.8573 | 1108.7539 | 0.4 | 0.6 | 0.63608 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 880422.6783 | 1320634.0175 | 1400055.3834 | 603103.5396 | 880422.6783 | 1320634.0175 | 1400055.3834 | 1.05 | 2.2376 | 5.0347 | 5.6584 | 1743.0148 | 697.2059 | 1045.8089 | 1077.588 | 0.4 | 0.6 | 0.61823 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 965003.7203 | 1447505.5805 | 1491491.0667 | 631423.6042 | 965003.7203 | 1447505.5805 | 1491491.0667 | 1.05 | 2.4525 | 5.5181 | 5.8585 | 1742.9333 | 697.1733 | 1045.76 | 1048.1219 | 0.4 | 0.6 | 0.60136 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1050446.4052 | 1575669.6078 | 1579228.2991 | 658799.7483 | 1050446.4052 | 1575669.6078 | 1579228.2991 | 1.05 | 2.6695 | 6.0064 | 6.0335 | 1742.8509 | 697.1404 | 1019.7954 | 1019.7954 | 0.4 | 0.58513 | 0.58513 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1136778.8698 | 1662910.2862 | 1662910.2862 | 685353.6567 | 1136778.8698 | 1662910.2862 | 1662910.2862 | 1.05 | 2.8888 | 6.1816 | 6.1816 | 1742.7677 | 697.1071 | 991.6004 | 991.6004 | 0.4 | 0.56898 | 0.56898 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1224030.5958 | 1741123.1275 | 1741123.1275 | 711186.0819 | 1224030.5958 | 1741123.1275 | 1741123.1275 | 1.05 | 3.1103 | 6.2933 | 6.2933 | 1742.6835 | 697.0734 | 959.9367 | 959.9367 | 0.4 | 0.55084 | 0.55084 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1312232.4967 | 1807069.5431 | 1807069.5431 | 736381.7127 | 1312232.4967 | 1807069.5431 | 1807069.5431 | 1.05 | 3.3343 | 6.3231 | 6.3231 | 1742.5984 | 697.0394 | 837.759 | 837.759 | 0.4 | 0.48075 | 0.48075 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1401417.0151 | 1684337.7589 | 1684337.7589 | 761012.6926 | 1401417.0151 | 1684337.7589 | 1684337.7589 | 1.05 | 3.5607 | 5.1436 | 5.1436 | 1742.5123 | 697.0049 | 833.8488 | 833.8488 | 0.4 | 0.47853 | 0.47853 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1491618.2312 | 1784469.5635 | 1784469.5635 | 785141.2189 | 1491618.2312 | 1784469.5635 | 1784469.5635 | 1.05 | 3.7897 | 5.4239 | 5.4239 | 1742.4252 | 696.9701 | 829.3956 | 829.3956 | 0.4 | 0.476 | 0.476 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1582871.9852 | 1883620.5096 | 1883620.5096 | 808821.5033 | 1582871.9852 | 1883620.5096 | 1883620.5096 | 1.05 | 4.0214 | 5.6947 | 5.6947 | 1742.337 | 696.9348 | 824.2974 | 824.2974 | 0.4 | 0.4731 | 0.4731 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1675216.0133 | 1981356.2933 | 1981356.2933 | 832101.2758 | 1675216.0133 | 1981356.2933 | 1981356.2933 | 1.05 | 4.2558 | 5.9534 | 5.9534
590 | 1742.0957 | 696.8383 | 1045.2574 | 1393.6766 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 306949.4964 | 460424.2446 | 613898.9928 | 356208.5348 | 0.46419 | 460424.2446 | 613898.9928 | 1.05 | 1.05 | 1.7543 | 3.1187 | 1742.021 | 696.8084 | 1045.2126 | 1359.4872 | 0.4 | 0.6 | 0.78041 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 385251.297 | 577876.9455 | 751633.0308 | 399072.883 | 0.41435 | 577876.9455 | 751633.0308 | 1.05 | 1.05 | 2.2017 | 3.7247 | 1741.9457 | 696.7783 | 1045.1674 | 1307.9763 | 0.4 | 0.6 | 0.75087 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 464213.0573 | 696319.5859 | 871410.1366 | 438074.7529 | 464213.0573 | 696319.5859 | 871410.1366 | 1.05 | 1.179 | 2.6528 | 4.1547 | 1741.8698 | 696.7479 | 1045.1219 | 1261.4804 | 0.4 | 0.6 | 0.72421 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 543853.2126 | 815779.8189 | 984660.4746 | 474176.323 | 543853.2126 | 815779.8189 | 984660.4746 | 1.05 | 1.3813 | 3.1078 | 4.5278 | 1741.7932 | 696.7173 | 1045.0759 | 1219.1933 | 0.4 | 0.6 | 0.69996 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 624191.0122 | 936286.5183 | 1092278.8032 | 508004.2222 | 624191.0122 | 936286.5183 | 1092278.8032 | 1.05 | 1.5852 | 3.5667 | 4.8542 | 1741.7159 | 696.6864 | 1045.0295 | 1180.4667 | 0.4 | 0.6 | 0.67776 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 705246.5531 | 1057869.8297 | 1194971.1404 | 539993.6965 | 705246.5531 | 1057869.8297 | 1194971.1404 | 1.05 | 1.791 | 4.0297 | 5.1419 | 1741.6379 | 696.6552 | 1044.9827 | 1144.7647 | 0.4 | 0.6 | 0.65729 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 787040.8172 | 1180561.2257 | 1293289.1759 | 570461.7881 | 787040.8172 | 1180561.2257 | 1293289.1759 | 1.05 | 1.9986 | 4.4969 | 5.3967 | 1741.5591 | 696.6237 | 1044.9355 | 1111.628 | 0.4 | 0.6 | 0.63829 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 869595.7107 | 1304393.5661 | 1387645.8618 | 599648.0749 | 869595.7107 | 1304393.5661 | 1387645.8618 | 1.05 | 2.2082 | 4.9684 | 5.6228 | 1741.4796 | 696.5919 | 1044.8878 | 1080.6388 | 0.4 | 0.6 | 0.62053 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 952934.1095 | 1429401.1643 | 1478308.3718 | 627738.9817 | 952934.1095 | 1429401.1643 | 1478308.3718 | 1.05 | 2.4197 | 5.4443 | 5.8232 | 1741.3993 | 696.5597 | 1044.8396 | 1051.3756 | 0.4 | 0.6 | 0.60375 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1037079.9073 | 1555619.8609 | 1565351.016 | 654883.0997 | 1037079.9073 | 1555619.8609 | 1565351.016 | 1.05 | 2.6332 | 5.9247 | 5.9991 | 1741.3183 | 696.5273 | 1023.3258 | 1023.3258 | 0.4 | 0.58767 | 0.58767 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1122058.0697 | 1648508.202 | 1648508.202 | 681201.2723 | 1122058.0697 | 1648508.202 | 1648508.202 | 1.05 | 2.8488 | 6.1492 | 6.1492 | 1741.2364 | 696.4945 | 995.6336 | 995.6336 | 0.4 | 0.5718 | 0.5718 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1207894.6945 | 1726676.193 | 1726676.193 | 706793.4807 | 1207894.6945 | 1726676.193 | 1726676.193 | 1.05 | 3.0666 | 6.2665 | 6.2665 | 1741.1536 | 696.4614 | 965.7685 | 965.7685 | 0.4 | 0.55467 | 0.55467 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1294617.0779 | 1795218.3897 | 1795218.3897 | 731743.6888 | 1294617.0779 | 1795218.3897 | 1795218.3897 | 1.05 | 3.2867 | 6.3198 | 6.3198 | 1741.07 | 696.428 | 837.7413 | 837.7413 | 0.4 | 0.48116 | 0.48116 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1382253.7884 | 1662729.1869 | 1662729.1869 | 756123.3427 | 1382253.7884 | 1662729.1869 | 1662729.1869 | 1.05 | 3.509 | 5.0775 | 5.0775 | 1740.9854 | 696.3942 | 833.9915 | 833.9915 | 0.4 | 0.47903 | 0.47903 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1470834.7486 | 1761450.2278 | 1761450.2278 | 779993.9561 | 1470834.7486 | 1761450.2278 | 1761450.2278 | 1.05 | 3.7337 | 5.3549 | 5.3549 | 1740.8999 | 696.36 | 829.7372 | 829.7372 | 0.4 | 0.47661 | 0.47661 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1560391.3273 | 1859260.7806 | 1859260.7806 | 803409.0582 | 1560391.3273 | 1859260.7806 | 1859260.7806 | 1.05 | 3.9608 | 5.6234 | 5.6234 | 1740.8134 | 696.3254 | 824.8833 | 824.8833 | 0.4 | 0.47385 | 0.47385 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1650956.44 | 1955761.6041 | 1955761.6041 | 826415.687 | 1650956.44 | 1955761.6041 | 1955761.6041 | 1.05 | 4.1905 | 5.8806 | 5.8806
600 | 1740.5508 | 696.2203 | 1044.3305 | 1392.4406 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 303605.1102 | 455407.6653 | 607210.2204 | 354419.8615 | 0.46695 | 455407.6653 | 607210.2204 | 1.05 | 1.05 | 1.7336 | 3.082 | 1740.477 | 696.1908 | 1044.2862 | 1360.9933 | 0.4 | 0.6 | 0.78197 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 380993.5094 | 571490.2642 | 744809.6238 | 397037.4806 | 0.41684 | 571490.2642 | 744809.6238 | 1.05 | 1.05 | 2.1754 | 3.695 | 1740.4026 | 696.161 | 1044.2416 | 1309.7769 | 0.4 | 0.6 | 0.75257 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 459007.6186 | 688511.4279 | 863589.819 | 435804.7358 | 459007.6186 | 688511.4279 | 863589.819 | 1.05 | 1.1648 | 2.6208 | 4.1231 | 1740.3276 | 696.131 | 1044.1966 | 1263.5295 | 0.4 | 0.6 | 0.72603 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 537664.036 | 806496.054 | 975900.1198 | 471679.3358 | 537664.036 | 806496.054 | 975900.1198 | 1.05 | 1.3643 | 3.0697 | 4.4948 | 1740.252 | 696.1008 | 1044.1512 | 1221.4568 | 0.4 | 0.6 | 0.70189 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 616980.0662 | 925470.0994 | 1082622.689 | 505284.9473 | 616980.0662 | 925470.0994 | 1082622.689 | 1.05 | 1.5655 | 3.5224 | 4.8203 | 1740.1757 | 696.0703 | 1044.1054 | 1182.9199 | 0.4 | 0.6 | 0.67977 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 696973.748 | 1045460.622 | 1184455.2424 | 537054.703 | 696973.748 | 1045460.622 | 1184455.2424 | 1.05 | 1.7684 | 3.9789 | 5.1073 | 1740.0987 | 696.0395 | 1044.0592 | 1147.391 | 0.4 | 0.6 | 0.65938 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 777663.8831 | 1166495.8246 | 1281945.3411 | 567304.048 | 777663.8831 | 1166495.8246 | 1281945.3411 | 1.05 | 1.9731 | 4.4394 | 5.3616 | 1740.0211 | 696.0084 | 1044.0126 | 1114.4196 | 0.4 | 0.6 | 0.64046 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 859070.069 | 1288605.1035 | 1375507.0595 | 596271.2943 | 859070.069 | 1288605.1035 | 1375507.0595 | 1.05 | 2.1795 | 4.9039 | 5.5876 | 1739.9427 | 695.9771 | 1043.9656 | 1083.5987 | 0.4 | 0.6 | 0.62278 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 941212.7339 | 1411819.1008 | 1465417.3301 | 624141.8221 | 941212.7339 | 1411819.1008 | 1465417.3301 | 1.05 | 2.3878 | 5.3726 | 5.7882 | 1739.8636 | 695.9454 | 1043.9182 | 1054.525 | 0.4 | 0.6 | 0.6061 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1024113.175 | 1536169.7624 | 1551778.1338 | 651063.3297 | 1024113.175 | 1536169.7624 | 1551778.1338 | 1.05 | 2.598 | 5.8455 | 5.9649 | 1739.7838 | 695.9135 | 1026.7251 | 1026.7251 | 0.4 | 0.59015 | 0.59015 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1107793.6008 | 1634397.8513 | 1634397.8513 | 677155.873 | 1107793.6008 | 1634397.8513 | 1634397.8513 | 1.05 | 2.8102 | 6.1168 | 6.1168 | 1739.7032 | 695.8813 | 999.4593 | 999.4593 | 0.4 | 0.5745 | 0.5745 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1192277.1778 | 1712407.8921 | 1712407.8921 | 702518.7195 | 1192277.1778 | 1712407.8921 | 1712407.8921 | 1.05 | 3.0243 | 6.2386 | 6.2386 | 1739.6217 | 695.8487 | 970.8335 | 970.8335 | 0.4 | 0.55807 | 0.55807 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1277588.0814 | 1782464.1132 | 1782464.1132 | 727235.1696 | 1277588.0814 | 1782464.1132 | 1782464.1132 | 1.05 | 3.2406 | 6.3078 | 6.3078 | 1739.5395 | 695.8158 | 837.6813 | 837.6813 | 0.4 | 0.48155 | 0.48155 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1363751.5526 | 1641798.2611 | 1641798.2611 | 751376.0396 | 1363751.5526 | 1641798.2611 | 1641798.2611 | 1.05 | 3.459 | 5.0132 | 5.0132 | 1739.4564 | 695.7826 | 834.079 | 834.079 | 0.4 | 0.47951 | 0.47951 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1450793.9604 | 1739159.4383 | 1739159.4383 | 775002.2327 | 1450793.9604 | 1739159.4383 | 1739159.4383 | 1.05 | 3.6796 | 5.2876 | 5.2876 | 1739.3725 | 695.749 | 830.0072 | 830.0072 | 0.4 | 0.47719 | 0.47719 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1538742.8709 | 1835673.0656 | 1835673.0656 | 798166.6764 | 1538742.8709 | 1835673.0656 | 1835673.0656 | 1.05 | 3.9024 | 5.5538 | 5.5538 | 1739.2876 | 695.715 | 825.3772 | 825.3772 | 0.4 | 0.47455 | 0.47455 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1627627.1239 | 1930971.9451 | 1930971.9451 | 820915.8069 | 1627627.1239 | 1930971.9451 | 1930971.9451 | 1.05 | 4.1276 | 5.8096 | 5.8096
610 | 1738.6944 | 695.4778 | 1043.2166 | 1390.9555 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 300278.3932 | 450417.5898 | 600556.7864 | 352660.8701 | 0.46978 | 450417.5898 | 600556.7864 | 1.05 | 1.05 | 1.7128 | 3.045 | 1738.6215 | 695.4486 | 1043.1729 | 1362.2058 | 0.4 | 0.6 | 0.7835 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 376762.3531 | 565143.5297 | 737981.0221 | 395037.2874 | 0.4194 | 565143.5297 | 737981.0221 | 1.05 | 1.05 | 2.149 | 3.6644 | 1738.548 | 695.4192 | 1043.1288 | 1311.2885 | 0.4 | 0.6 | 0.75424 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 453839.9523 | 680759.9285 | 855764.5413 | 433575.6475 | 453839.9523 | 680759.9285 | 855764.5413 | 1.05 | 1.1504 | 2.5885 | 4.0904 | 1738.4739 | 695.3896 | 1043.0844 | 1265.2934 | 0.4 | 0.6 | 0.72782 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 531526.1566 | 797289.2349 | 967136.3879 | 469229.2666 | 531526.1566 | 797289.2349 | 967136.3879 | 1.05 | 1.3473 | 3.0315 | 4.4606 | 1738.3992 | 695.3597 | 1043.0395 | 1223.4384 | 0.4 | 0.6 | 0.70377 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 609836.546 | 914754.819 | 1072966.1772 | 502618.9087 | 609836.546 | 914754.819 | 1072966.1772 | 1.05 | 1.5457 | 3.4779 | 4.785 | 1738.3239 | 695.3296 | 1042.9944 | 1185.0936 | 0.4 | 0.6 | 0.68174 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 688787.3368 | 1033181.0052 | 1173943.2321 | 534175.6436 | 688787.3368 | 1033181.0052 | 1173943.2321 | 1.05 | 1.7458 | 3.928 | 5.0713 | 1738.248 | 695.2992 | 1042.9488 | 1149.7396 | 0.4 | 0.6 | 0.66144 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 768395.4059 | 1152593.1089 | 1270610.6699 | 564213.3654 | 768395.4059 | 1152593.1089 | 1270610.6699 | 1.05 | 1.9475 | 4.3818 | 5.3251 | 1738.1714 | 695.2686 | 1042.9029 | 1116.9336 | 0.4 | 0.6 | 0.64259 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 848678.3161 | 1273017.4741 | 1363382.9192 | 592969.1643 | 848678.3161 | 1273017.4741 | 1363382.9192 | 1.05 | 2.1509 | 4.8394 | 5.5509 | 1738.0942 | 695.2377 | 1042.8565 | 1086.2789 | 0.4 | 0.6 | 0.62498 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 929654.3444 | 1394481.5166 | 1452544.8646 | 620627.4194 | 929654.3444 | 1394481.5166 | 1452544.8646 | 1.05 | 2.356 | 5.3009 | 5.7516 | 1738.0163 | 695.2065 | 1042.8098 | 1057.3882 | 0.4 | 0.6 | 0.60839 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1011342.5123 | 1517013.7685 | 1538221.6038 | 647334.9802 | 1011342.5123 | 1517013.7685 | 1538221.6038 | 1.05 | 2.5629 | 5.7665 | 5.9288 | 1737.9376 | 695.175 | 1029.821 | 1029.821 | 0.4 | 0.59255 | 0.59255 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1093762.6193 | 1620282.111 | 1620282.111 | 673211.1615 | 1093762.6193 | 1620282.111 | 1620282.111 | 1.05 | 2.7716 | 6.0823 | 6.0823 | 1737.8583 | 695.1433 | 1002.9277 | 1002.9277 | 0.4 | 0.57711 | 0.57711 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1176935.2787 | 1698039.8439 | 1698039.8439 | 698354.5649 | 1176935.2787 | 1698039.8439 | 1698039.8439 | 1.05 | 2.9822 | 6.2077 | 6.2077 | 1737.7781 | 695.1113 | 975.2291 | 975.2291 | 0.4 | 0.56119 | 0.56119 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1260881.9579 | 1768995.6484 | 1768995.6484 | 722847.879 | 1260881.9579 | 1768995.6484 | 1768995.6484 | 1.05 | 3.1948 | 6.2885 | 6.2885 | 1737.6973 | 695.0789 | 837.4334 | 837.4334 | 0.4 | 0.48192 | 0.48192 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1345625.0216 | 1621213.6091 | 1621213.6091 | 746761.3452 | 1345625.0216 | 1621213.6091 | 1621213.6091 | 1.05 | 3.4094 | 4.9489 | 4.9489 | 1737.6156 | 695.0462 | 833.968 | 833.968 | 0.4 | 0.47995 | 0.47995 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1431187.78 | 1717245.2523 | 1717245.2523 | 770155.3163 | 1431187.78 | 1717245.2523 | 1717245.2523 | 1.05 | 3.626 | 5.2203 | 5.2203 | 1737.5331 | 695.0132 | 830.0647 | 830.0647 | 0.4 | 0.47773 | 0.47773 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1517594.5412 | 1812485.91 | 1812485.91 | 793082.1834 | 1517594.5412 | 1812485.91 | 1812485.91 | 1.05 | 3.8447 | 5.4841 | 5.4841 | 1737.4498 | 694.9799 | 825.641 | 825.641 | 0.4 | 0.4752 | 0.4752 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1604870.6695 | 1906597.6506 | 1906597.6506 | 815587.8524 | 1604870.6695 | 1906597.6506 | 1906597.6506 | 1.05 | 4.0656 | 5.7381 | 5.7381
620 | 1736.836 | 694.7344 | 1042.1016 | 1389.4688 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 297021.2749 | 445531.9124 | 594042.5499 | 350930.5984 | 0.4726 | 445531.9124 | 594042.5499 | 1.05 | 1.05 | 1.6924 | 3.0087 | 1736.7639 | 694.7056 | 1042.0583 | 1363.3678 | 0.4 | 0.6 | 0.785 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 372622.6396 | 558933.9594 | 731276.3124 | 393071.0768 | 0.42195 | 558933.9594 | 731276.3124 | 1.05 | 1.05 | 2.1231 | 3.6342 | 1736.6913 | 694.6765 | 1042.0148 | 1312.745 | 0.4 | 0.6 | 0.75589 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 448787.6733 | 673181.5099 | 848083.6211 | 431385.9628 | 448787.6733 | 673181.5099 | 848083.6211 | 1.05 | 1.1364 | 2.5569 | 4.0582 | 1736.6181 | 694.6472 | 1041.9709 | 1266.9983 | 0.4 | 0.6 | 0.72958 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 525529.8909 | 788294.8364 | 958537.5606 | 466824.2524 | 525529.8909 | 788294.8364 | 958537.5606 | 1.05 | 1.3307 | 2.9941 | 4.4269 | 1736.5444 | 694.6177 | 1041.9266 | 1225.3569 | 0.4 | 0.6 | 0.70563 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 602863.3427 | 904295.014 | 1063495.4015 | 500003.8623 | 602863.3427 | 904295.014 | 1063495.4015 | 1.05 | 1.5264 | 3.4345 | 4.7502 | 1736.47 | 694.588 | 1041.882 | 1187.2003 | 0.4 | 0.6 | 0.68369 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 680802.6315 | 1021203.9473 | 1163638.1185 | 531353.8458 | 680802.6315 | 1021203.9473 | 1163638.1185 | 1.05 | 1.7237 | 3.8783 | 5.0357 | 1736.3951 | 694.558 | 1041.8371 | 1152.0167 | 0.4 | 0.6 | 0.66345 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 759362.9331 | 1139044.3996 | 1259504.2049 | 561186.5871 | 759362.9331 | 1139044.3996 | 1259504.2049 | 1.05 | 1.9225 | 4.3257 | 5.289 | 1736.3196 | 694.5278 | 1041.7917 | 1119.3711 | 0.4 | 0.6 | 0.64468 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 838560.0162 | 1257840.0243 | 1351507.8542 | 589737.9939 | 838560.0162 | 1257840.0243 | 1351507.8542 | 1.05 | 2.1229 | 4.7766 | 5.5145 | 1736.2434 | 694.4974 | 1041.746 | 1088.8759 | 0.4 | 0.6 | 0.62714 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 918410.2655 | 1377615.3982 | 1439940.4231 | 617191.4824 | 918410.2655 | 1377615.3982 | 1439940.4231 | 1.05 | 2.325 | 5.2312 | 5.7153 | 1736.1666 | 694.4666 | 1041.6999 | 1060.158 | 0.4 | 0.6 | 0.61063 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 998930.7056 | 1498396.0583 | 1524946.3967 | 643693.092 | 998930.7056 | 1498396.0583 | 1524946.3967 | 1.05 | 2.5287 | 5.6896 | 5.8931 | 1736.0891 | 694.4356 | 1032.8045 | 1032.8045 | 0.4 | 0.5949 | 0.5949 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1080139.0273 | 1606444.7613 | 1606444.7613 | 669361.4351 | 1080139.0273 | 1606444.7613 | 1606444.7613 | 1.05 | 2.7342 | 6.0478 | 6.0478 | 1736.0109 | 694.4044 | 1006.2376 | 1006.2376 | 0.4 | 0.57963 | 0.57963 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1162053.6163 | 1683892.1948 | 1683892.1948 | 694294.4889 | 1162053.6163 | 1683892.1948 | 1683892.1948 | 1.05 | 2.9414 | 6.1763 | 6.1763 | 1735.9321 | 694.3728 | 979.2643 | 979.2643 | 0.4 | 0.56411 | 0.56411 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1244693.5843 | 1755373.9618 | 1755373.9618 | 718574.3732 | 1244693.5843 | 1755373.9618 | 1755373.9618 | 1.05 | 3.1504 | 6.2659 | 6.2659 | 1735.8525 | 694.341 | 945.7748 | 945.7748 | 0.4 | 0.54485 | 0.54485 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1328078.8025 | 1809000.8995 | 1809000.8995 | 742270.8006 | 1328078.8025 | 1809000.8995 | 1809000.8995 | 1.05 | 3.3613 | 6.2365 | 6.2365 | 1735.7722 | 694.3089 | 833.8112 | 833.8112 | 0.4 | 0.48037 | 0.48037 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1412229.939 | 1695978.8626 | 1695978.8626 | 765443.6226 | 1412229.939 | 1695978.8626 | 1695978.8626 | 1.05 | 3.5742 | 5.1547 | 5.1547 | 1735.6911 | 694.2764 | 830.0634 | 830.0634 | 0.4 | 0.47823 | 0.47823 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1497168.4994 | 1789985.5503 | 1789985.5503 | 788144.7473 | 1497168.4994 | 1789985.5503 | 1789985.5503 | 1.05 | 3.7889 | 5.416 | 5.416 | 1735.6092 | 694.2437 | 825.8297 | 825.8297 | 0.4 | 0.47582 | 0.47582 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1582916.8705 | 1882940.7821 | 1882940.7821 | 810419.6081 | 1582916.8705 | 1882940.7821 | 1882940.7821 | 1.05 | 4.0058 | 5.6682 | 5.6682
630 | 1734.9755 | 693.9902 | 1040.9853 | 1387.9804 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 293831.312 | 440746.968 | 587662.624 | 349228.1365 | 0.47541 | 440746.968 | 587662.624 | 1.05 | 1.05 | 1.6724 | 2.9732 | 1734.9042 | 693.9617 | 1040.9425 | 1364.4808 | 0.4 | 0.6 | 0.78649 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 368570.9731 | 552856.4597 | 724691.3431 | 391137.6952 | 0.42449 | 552856.4597 | 724691.3431 | 1.05 | 1.05 | 2.0978 | 3.6044 | 1734.8325 | 693.933 | 1040.8995 | 1314.1483 | 0.4 | 0.6 | 0.75751 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 443846.2577 | 665769.3866 | 840541.9488 | 429234.2538 | 443846.2577 | 665769.3866 | 840541.9488 | 1.05 | 1.1227 | 2.5261 | 4.0264 | 1734.7602 | 693.9041 | 1040.8561 | 1268.646 | 0.4 | 0.6 | 0.73131 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 519669.3893 | 779504.084 | 950097.4769 | 464462.557 | 519669.3893 | 779504.084 | 950097.4769 | 1.05 | 1.3144 | 2.9575 | 4.3936 | 1734.6873 | 693.8749 | 1040.8124 | 1227.2147 | 0.4 | 0.6 | 0.70746 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 596053.0582 | 894079.5873 | 1054203.0528 | 497437.7256 | 596053.0582 | 894079.5873 | 1054203.0528 | 1.05 | 1.5076 | 3.3921 | 4.7159 | 1734.6139 | 693.8456 | 1040.7684 | 1189.2425 | 0.4 | 0.6 | 0.68559 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 673010.4362 | 1009515.6543 | 1153531.3557 | 528586.8389 | 673010.4362 | 1009515.6543 | 1153531.3557 | 1.05 | 1.7022 | 3.8299 | 5.0005 | 1734.54 | 693.816 | 1040.724 | 1154.2253 | 0.4 | 0.6 | 0.66544 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 750555.1925 | 1125832.7888 | 1248616.1072 | 558220.8092 | 750555.1925 | 1125832.7888 | 1248616.1072 | 1.05 | 1.8982 | 4.271 | 5.2533 | 1734.4654 | 693.7862 | 1040.6793 | 1121.7354 | 0.4 | 0.6 | 0.64673 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 828701.5107 | 1243052.2661 | 1339870.7637 | 586574.3961 | 828701.5107 | 1243052.2661 | 1339870.7637 | 1.05 | 2.0957 | 4.7154 | 5.4786 | 1734.3903 | 693.7561 | 1040.6342 | 1091.3937 | 0.4 | 0.6 | 0.62927 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 907464.1065 | 1361196.1597 | 1427591.9029 | 613830.087 | 907464.1065 | 1361196.1597 | 1427591.9029 | 1.05 | 2.2948 | 5.1634 | 5.6794 | 1734.3146 | 693.7258 | 1040.5887 | 1062.8396 | 0.4 | 0.6 | 0.61283 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 986858.2474 | 1480287.3711 | 1511940.3112 | 640133.1443 | 986858.2474 | 1480287.3711 | 1511940.3112 | 1.05 | 2.4955 | 5.6149 | 5.8576 | 1734.2382 | 693.6953 | 1035.6839 | 1035.6839 | 0.4 | 0.5972 | 0.5972 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1066899.7736 | 1592876.55 | 1592876.55 | 665601.5127 | 1066899.7736 | 1592876.55 | 1592876.55 | 1.05 | 2.6978 | 6.0135 | 6.0135 | 1734.1612 | 693.6645 | 1009.4064 | 1009.4064 | 0.4 | 0.58207 | 0.58207 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1147605.1205 | 1669971.5931 | 1669971.5931 | 690332.5795 | 1147605.1205 | 1669971.5931 | 1669971.5931 | 1.05 | 2.9017 | 6.1446 | 6.1446 | 1734.0835 | 693.6334 | 983.0202 | 983.0202 | 0.4 | 0.56688 | 0.56688 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1228991.3432 | 1741731.6858 | 1741731.6858 | 714407.9328 | 1228991.3432 | 1741731.6858 | 1741731.6858 | 1.05 | 3.1074 | 6.2411 | 6.2411 | 1734.0052 | 693.6021 | 952.7788 | 952.7788 | 0.4 | 0.54947 | 0.54947 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1311076.1427 | 1800983.0554 | 1800983.0554 | 737896.7945 | 1311076.1427 | 1800983.0554 | 1800983.0554 | 1.05 | 3.3148 | 6.2549 | 6.2549 | 1733.9261 | 693.5705 | 833.6126 | 833.6126 | 0.4 | 0.48077 | 0.48077 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1393877.8955 | 1675322.511 | 1675322.511 | 760858.5562 | 1393877.8955 | 1675322.511 | 1675322.511 | 1.05 | 3.524 | 5.0907 | 5.0907 | 1733.8464 | 693.5386 | 830.0086 | 830.0086 | 0.4 | 0.47871 | 0.47871 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1477415.6839 | 1768132.0901 | 1768132.0901 | 783344.6869 | 1477415.6839 | 1768132.0901 | 1768132.0901 | 1.05 | 3.735 | 5.3495 | 5.3495 | 1733.7659 | 693.5064 | 825.9503 | 825.9503 | 0.4 | 0.47639 | 0.47639 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1561709.3308 | 1859960.2218 | 1859960.2218 | 805400.1947 | 1561709.3308 | 1859960.2218 | 1859960.2218 | 1.05 | 3.9479 | 5.5998 | 5.5998
640 | 1733.1129 | 693.2452 | 1039.8678 | 1386.4903 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 290706.1925 | 436059.2887 | 581412.385 | 347552.6233 | 0.47822 | 436059.2887 | 581412.385 | 1.05 | 1.05 | 1.6529 | 2.9384 | 1733.0425 | 693.217 | 1039.8255 | 1365.5462 | 0.4 | 0.6 | 0.78795 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 364604.1545 | 546906.2318 | 718222.1951 | 389236.0558 | 0.42702 | 546906.2318 | 718222.1951 | 1.05 | 1.05 | 2.073 | 3.575 | 1732.9715 | 693.1886 | 1039.7829 | 1315.4998 | 0.4 | 0.6 | 0.7591 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 439011.4618 | 658517.1927 | 833134.7223 | 427119.1813 | 439011.4618 | 658517.1927 | 833134.7223 | 1.05 | 1.1093 | 2.4959 | 3.995 | 1732.9001 | 693.16 | 1039.7401 | 1270.2384 | 0.4 | 0.6 | 0.73301 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 513939.1862 | 770908.7793 | 941810.3713 | 462142.5588 | 513939.1862 | 770908.7793 | 941810.3713 | 1.05 | 1.2986 | 2.9218 | 4.3608 | 1732.8281 | 693.1313 | 1039.6969 | 1229.0137 | 0.4 | 0.6 | 0.70925 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 589398.8073 | 884098.211 | 1045082.3183 | 494918.5614 | 589398.8073 | 884098.211 | 1045082.3183 | 1.05 | 1.4892 | 3.3506 | 4.6819 | 1732.7557 | 693.1023 | 1039.6534 | 1191.2226 | 0.4 | 0.6 | 0.68747 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 665402.2249 | 998103.3374 | 1143615.0063 | 525872.3339 | 665402.2249 | 998103.3374 | 1143615.0063 | 1.05 | 1.6811 | 3.7825 | 4.9658 | 1732.6826 | 693.0731 | 1039.6096 | 1156.3682 | 0.4 | 0.6 | 0.66739 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 741961.7718 | 1112942.6577 | 1237937.2654 | 555313.3504 | 741961.7718 | 1112942.6577 | 1237937.2654 | 1.05 | 1.8745 | 4.2175 | 5.2181 | 1732.6091 | 693.0436 | 1039.5654 | 1124.0296 | 0.4 | 0.6 | 0.64875 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 819090.2273 | 1228635.341 | 1328461.3864 | 583475.2544 | 819090.2273 | 1228635.341 | 1328461.3864 | 1.05 | 2.0692 | 4.6558 | 5.443 | 1732.5349 | 693.014 | 1039.521 | 1093.836 | 0.4 | 0.6 | 0.63135 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 896800.8323 | 1345201.2484 | 1415488.1052 | 610539.634 | 896800.8323 | 1345201.2484 | 1415488.1052 | 1.05 | 2.2654 | 5.0973 | 5.6438 | 1732.4602 | 692.9841 | 1039.4761 | 1065.4378 | 0.4 | 0.6 | 0.61499 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 975107.3043 | 1462660.9564 | 1499191.9393 | 636651.0048 | 975107.3043 | 1462660.9564 | 1499191.9393 | 1.05 | 2.4632 | 5.5421 | 5.8224 | 1732.3849 | 692.954 | 1038.4661 | 1038.4661 | 0.4 | 0.59944 | 0.59944 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1054023.8547 | 1579568.2268 | 1579568.2268 | 661926.6725 | 1054023.8547 | 1579568.2268 | 1579568.2268 | 1.05 | 2.6624 | 5.9792 | 5.9792 | 1732.309 | 692.9236 | 1012.4479 | 1012.4479 | 0.4 | 0.58445 | 0.58445 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1133565.2065 | 1656280.279 | 1656280.279 | 686463.4657 | 1133565.2065 | 1656280.279 | 1656280.279 | 1.05 | 2.8632 | 6.1125 | 6.1125 | 1732.2325 | 692.893 | 986.5495 | 986.5495 | 0.4 | 0.56952 | 0.56952 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1213746.6135 | 1728147.1192 | 1728147.1192 | 710342.4712 | 1213746.6135 | 1728147.1192 | 1728147.1192 | 1.05 | 3.0656 | 6.2146 | 6.2146 | 1732.1554 | 692.8622 | 958.1648 | 958.1648 | 0.4 | 0.55316 | 0.55316 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1294583.8815 | 1790290.7695 | 1790290.7695 | 733632.4536 | 1294583.8815 | 1790290.7695 | 1790290.7695 | 1.05 | 3.2696 | 6.2529 | 6.2529 | 1732.0776 | 692.831 | 833.3758 | 833.3758 | 0.4 | 0.48114 | 0.48114 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1376093.3905 | 1655241.8547 | 1655241.8547 | 756392.3789 | 1376093.3905 | 1655241.8547 | 1655241.8547 | 1.05 | 3.4753 | 5.0283 | 5.0283 | 1731.9991 | 692.7997 | 829.9052 | 829.9052 | 0.4 | 0.47916 | 0.47916 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1458292.1195 | 1746889.2148 | 1746889.2148 | 778673.3136 | 1458292.1195 | 1746889.2148 | 1746889.2148 | 1.05 | 3.6827 | 5.2846 | 5.2846 | 1731.92 | 692.768 | 826.0091 | 826.0091 | 0.4 | 0.47693 | 0.47693 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1541197.6724 | 1837618.5042 | 1837618.5042 | 800519.8793 | 1541197.6724 | 1837618.5042 | 1837618.5042 | 1.05 | 3.8919 | 5.5329 | 5.5329
650 | 1731.2483 | 692.4993 | 1038.749 | 1384.9987 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 287643.7258 | 431465.5888 | 575287.4517 | 345903.2419 | 0.48102 | 431465.5888 | 575287.4517 | 1.05 | 1.05 | 1.6337 | 2.9044 | 1731.1786 | 692.4715 | 1038.7072 | 1366.5653 | 0.4 | 0.6 | 0.78938 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 360719.1651 | 541078.7476 | 711865.1628 | 387365.1326 | 0.42955 | 541078.7476 | 711865.1628 | 1.05 | 1.05 | 2.0487 | 3.546 | 1731.1085 | 692.4434 | 1038.6651 | 1316.8013 | 0.4 | 0.6 | 0.76067 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 434279.297 | 651418.9454 | 825857.4203 | 425039.4868 | 434279.297 | 651418.9454 | 825857.4203 | 1.05 | 1.0961 | 2.4663 | 3.9641 | 1731.0379 | 692.4152 | 1038.6227 | 1271.7773 | 0.4 | 0.6 | 0.73469 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 508334.1646 | 762501.2469 | 933670.8372 | 459862.7401 | 508334.1646 | 762501.2469 | 933670.8372 | 1.05 | 1.283 | 2.8868 | 4.3283 | 1730.9668 | 692.3867 | 1038.5801 | 1230.7559 | 0.4 | 0.6 | 0.71102 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 582894.1681 | 874341.2521 | 1036126.833 | 492444.5637 | 582894.1681 | 874341.2521 | 1036126.833 | 1.05 | 1.4711 | 3.3101 | 4.6484 | 1730.8952 | 692.3581 | 1038.5371 | 1193.1426 | 0.4 | 0.6 | 0.68932 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 657970.0744 | 986955.1115 | 1133881.6801 | 523208.204 | 657970.0744 | 986955.1115 | 1133881.6801 | 1.05 | 1.6606 | 3.7362 | 4.9315 | 1730.8231 | 692.3292 | 1038.4939 | 1158.4476 | 0.4 | 0.6 | 0.6693 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 733573.0281 | 1100359.5422 | 1227459.2205 | 552461.7288 | 733573.0281 | 1100359.5422 | 1227459.2205 | 1.05 | 1.8513 | 4.1654 | 5.1832 | 1730.7505 | 692.3002 | 1038.4503 | 1126.2567 | 0.4 | 0.6 | 0.65073 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 809714.5629 | 1214571.8444 | 1317270.2135 | 580437.6933 | 809714.5629 | 1214571.8444 | 1317270.2135 | 1.05 | 2.0433 | 4.5975 | 5.4079 | 1730.6773 | 692.2709 | 1038.4064 | 1096.2061 | 0.4 | 0.6 | 0.6334 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 886406.6127 | 1329609.9191 | 1403618.6471 | 607316.8138 | 886406.6127 | 1329609.9191 | 1403618.6471 | 1.05 | 2.2368 | 5.0328 | 5.6086 | 1730.6036 | 692.2414 | 1038.3622 | 1067.9568 | 0.4 | 0.6 | 0.6171 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 963661.5251 | 1445492.2876 | 1486690.6146 | 633242.8846 | 963661.5251 | 1445492.2876 | 1486690.6146 | 1.05 | 2.4316 | 5.4712 | 5.7875 | 1730.5294 | 692.2117 | 1038.3176 | 1041.1573 | 0.4 | 0.6 | 0.60164 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1041492.074 | 1562238.111 | 1566510.7021 | 658332.5989 | 1041492.074 | 1562238.111 | 1566510.7021 | 1.05 | 2.6279 | 5.9128 | 5.9452 | 1730.4545 | 692.1818 | 1015.3735 | 1015.3735 | 0.4 | 0.58677 | 0.58677 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1119911.4748 | 1642817.6132 | 1642817.6132 | 682682.2522 | 1119911.4748 | 1642817.6132 | 1642817.6132 | 1.05 | 2.8257 | 6.0804 | 6.0804 | 1730.3791 | 692.1516 | 989.8887 | 989.8887 | 0.4 | 0.57206 | 0.57206 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1198933.3991 | 1714668.5267 | 1714668.5267 | 706372.4577 | 1198933.3991 | 1714668.5267 | 1714668.5267 | 1.05 | 3.0249 | 6.187 | 6.187 | 1730.3031 | 692.1212 | 962.7668 | 962.7668 | 0.4 | 0.55642 | 0.55642 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1278571.9916 | 1778541.8779 | 1778541.8779 | 729471.5502 | 1278571.9916 | 1778541.8779 | 1778541.8779 | 1.05 | 3.2257 | 6.2417 | 6.2417 | 1730.2265 | 692.0906 | 833.1039 | 833.1039 | 0.4 | 0.4815 | 0.4815 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1358841.8879 | 1635705.5637 | 1635705.5637 | 752038.0993 | 1358841.8879 | 1635705.5637 | 1635705.5637 | 1.05 | 3.4281 | 4.9673 | 4.9673 | 1730.1493 | 692.0597 | 829.7573 | 829.7573 | 0.4 | 0.47959 | 0.47959 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1439758.2331 | 1726223.7706 | 1726223.7706 | 774122.7998 | 1439758.2331 | 1726223.7706 | 1726223.7706 | 1.05 | 3.632 | 5.2211 | 5.2211 | 1730.0714 | 692.0286 | 826.0116 | 826.0116 | 0.4 | 0.47744 | 0.47744 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1521336.7031 | 1815881.3816 | 1815881.3816 | 795769.9198 | 1521336.7031 | 1815881.3816 | 1815881.3816 | 1.05 | 3.8376 | 5.4675 | 5.4675
660 | 1729.3816 | 691.7526 | 1037.629 | 1383.5053 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 284641.8337 | 426962.7506 | 569283.6674 | 344279.217 | 0.48381 | 426962.7506 | 569283.6674 | 1.05 | 1.05 | 1.6149 | 2.8709 | 1729.3127 | 691.7251 | 1037.5876 | 1367.5394 | 0.4 | 0.6 | 0.7908 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 356913.1518 | 535369.7277 | 705616.7369 | 385523.9558 | 0.43206 | 535369.7277 | 705616.7369 | 1.05 | 1.05 | 2.0249 | 3.5174 | 1729.2434 | 691.6973 | 1037.546 | 1318.0539 | 0.4 | 0.6 | 0.76221 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 429646.0079 | 644469.0119 | 818705.778 | 422993.9854 | 429646.0079 | 644469.0119 | 818705.778 | 1.05 | 1.0833 | 2.4374 | 3.9335 | 1729.1736 | 691.6694 | 1037.5041 | 1273.2641 | 0.4 | 0.6 | 0.73634 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 502849.5249 | 754274.2874 | 925673.7944 | 457621.6778 | 502849.5249 | 754274.2874 | 925673.7944 | 1.05 | 1.2678 | 2.8526 | 4.2963 | 1729.1033 | 691.6413 | 1037.462 | 1232.4432 | 0.4 | 0.6 | 0.71276 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 576533.1382 | 864799.7074 | 1027330.6379 | 490014.0451 | 576533.1382 | 864799.7074 | 1027330.6379 | 1.05 | 1.4535 | 3.2704 | 4.6152 | 1729.0326 | 691.613 | 1037.4195 | 1195.0047 | 0.4 | 0.6 | 0.69114 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 650706.6046 | 976059.9069 | 1124324.4811 | 520592.4696 | 650706.6046 | 976059.9069 | 1124324.4811 | 1.05 | 1.6405 | 3.691 | 4.8975 | 1728.9613 | 691.5845 | 1037.3768 | 1160.4659 | 0.4 | 0.6 | 0.67119 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 725380.0106 | 1088070.0159 | 1217174.1016 | 549663.6414 | 725380.0106 | 1088070.0159 | 1217174.1016 | 1.05 | 1.8286 | 4.1144 | 5.1487 | 1728.8896 | 691.5559 | 1037.3338 | 1128.419 | 0.4 | 0.6 | 0.65268 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 800563.7818 | 1200845.6728 | 1306288.414 | 577459.0537 | 800563.7818 | 1200845.6728 | 1306288.414 | 1.05 | 2.0181 | 4.5407 | 5.3731 | 1728.8174 | 691.527 | 1037.2905 | 1098.5072 | 0.4 | 0.6 | 0.63541 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 876268.6926 | 1314403.0389 | 1391973.8826 | 604158.5747 | 876268.6926 | 1314403.0389 | 1391973.8826 | 1.05 | 2.2088 | 4.9699 | 5.5738 | 1728.7447 | 691.4979 | 1037.2468 | 1070.4004 | 0.4 | 0.6 | 0.61918 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 952505.8761 | 1428758.8141 | 1474426.3603 | 629905.3008 | 952505.8761 | 1428758.8141 | 1474426.3603 | 1.05 | 2.4009 | 5.402 | 5.7529 | 1728.6714 | 691.4686 | 1037.2029 | 1043.7629 | 0.4 | 0.6 | 0.60379 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1029286.8354 | 1543930.2531 | 1553695.1452 | 654815.3357 | 1029286.8354 | 1543930.2531 | 1553695.1452 | 1.05 | 2.5943 | 5.8372 | 5.9113 | 1728.5976 | 691.4391 | 1018.1928 | 1018.1928 | 0.4 | 0.58903 | 0.58903 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1106623.4549 | 1629581.0695 | 1629581.0695 | 678984.4648 | 1106623.4549 | 1629581.0695 | 1629581.0695 | 1.05 | 2.7891 | 6.0481 | 6.0481 | 1728.5233 | 691.4093 | 993.0646 | 993.0646 | 0.4 | 0.57452 | 0.57452 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1184528.0125 | 1701326.3142 | 1701326.3142 | 702492.8507 | 1184528.0125 | 1701326.3142 | 1701326.3142 | 1.05 | 2.9854 | 6.1586 | 6.1586 | 1728.4484 | 691.3794 | 966.8758 | 966.8758 | 0.4 | 0.55939 | 0.55939 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1263013.1932 | 1766290.6009 | 1766290.6009 | 725408.4229 | 1263013.1932 | 1766290.6009 | 1766290.6009 | 1.05 | 3.183 | 6.2251 | 6.2251 | 1728.3729 | 691.3492 | 832.7996 | 832.7996 | 0.4 | 0.48184 | 0.48184 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1342092.1023 | 1616684.9749 | 1616684.9749 | 747789.3793 | 1342092.1023 | 1616684.9749 | 1616684.9749 | 1.05 | 3.3822 | 4.9077 | 4.9077 | 1728.2969 | 691.3188 | 829.5686 | 829.5686 | 0.4 | 0.47999 | 0.47999 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1421778.2815 | 1706105.4038 | 1706105.4038 | 769686.0692 | 1421778.2815 | 1706105.4038 | 1706105.4038 | 1.05 | 3.5828 | 5.1591 | 5.1591 | 1728.2202 | 691.2881 | 825.9627 | 825.9627 | 0.4 | 0.47793 | 0.47793 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1502085.7242 | 1794717.4567 | 1794717.4567 | 791142.4344 | 1502085.7242 | 1794717.4567 | 1794717.4567 | 1.05 | 3.785 | 5.4035 | 5.4035
670 | 1727.5128 | 691.0051 | 1036.5077 | 1382.0103 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 281698.5419 | 422547.8128 | 563397.0837 | 342679.811 | 0.48659 | 422547.8128 | 563397.0837 | 1.05 | 1.05 | 1.5965 | 2.8382 | 1727.4447 | 690.9779 | 1036.4668 | 1368.4696 | 0.4 | 0.6 | 0.79219 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 353183.4145 | 529775.1218 | 699473.5886 | 383711.6069 | 0.43457 | 529775.1218 | 699473.5886 | 1.05 | 1.05 | 2.0015 | 3.4892 | 1727.3761 | 690.9504 | 1036.4257 | 1319.2593 | 0.4 | 0.6 | 0.76374 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 425108.0535 | 637662.0803 | 811675.7656 | 420981.5594 | 425108.0535 | 637662.0803 | 811675.7656 | 1.05 | 1.0707 | 2.409 | 3.9033 | 1727.3071 | 690.9228 | 1036.3843 | 1274.7005 | 0.4 | 0.6 | 0.73797 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 497480.7568 | 746221.1352 | 917814.4602 | 455418.0343 | 497480.7568 | 746221.1352 | 917814.4602 | 1.05 | 1.2529 | 2.8191 | 4.2646 | 1727.2377 | 690.8951 | 1036.3426 | 1234.0771 | 0.4 | 0.6 | 0.71448 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 570310.0968 | 855465.1452 | 1018688.1427 | 487625.4257 | 570310.0968 | 855465.1452 | 1018688.1427 | 1.05 | 1.4363 | 3.2316 | 4.5825 | 1727.1678 | 690.8671 | 1036.3007 | 1196.8107 | 0.4 | 0.6 | 0.69293 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 643604.9275 | 965407.3912 | 1114936.9604 | 518023.2833 | 643604.9275 | 965407.3912 | 1114936.9604 | 1.05 | 1.6208 | 3.6468 | 4.864 | 1727.0974 | 690.839 | 1036.2584 | 1162.4253 | 0.4 | 0.6 | 0.67305 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 717374.3914 | 1076061.5872 | 1207074.568 | 546916.9464 | 717374.3914 | 1076061.5872 | 1207074.568 | 1.05 | 1.8065 | 4.0646 | 5.1146 | 1727.0266 | 690.8106 | 1036.2159 | 1130.5192 | 0.4 | 0.6 | 0.6546 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 791627.9273 | 1187441.891 | 1295507.7673 | 574536.87 | 791627.9273 | 1187441.891 | 1295507.7673 | 1.05 | 1.9934 | 4.4852 | 5.3387 | 1726.9553 | 690.7821 | 1036.1732 | 1100.742 | 0.4 | 0.6 | 0.63739 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 866375.2779 | 1299562.9169 | 1380544.8329 | 601062.0959 | 866375.2779 | 1299562.9169 | 1380544.8329 | 1.05 | 2.1815 | 4.9085 | 5.5393 | 1726.8835 | 690.7534 | 1036.1301 | 1072.7722 | 0.4 | 0.6 | 0.62122 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 941626.4984 | 1412439.7476 | 1462389.8374 | 626635.0434 | 941626.4984 | 1412439.7476 | 1462389.8374 | 1.05 | 2.3709 | 5.3346 | 5.7186 | 1726.8112 | 690.7245 | 1036.0867 | 1046.2875 | 0.4 | 0.6 | 0.60591 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1017391.9651 | 1526087.9476 | 1541113.0421 | 651371.2469 | 1017391.9651 | 1526087.9476 | 1541113.0421 | 1.05 | 2.5616 | 5.7636 | 5.8776 | 1726.7384 | 690.6954 | 1020.9136 | 1020.9136 | 0.4 | 0.59124 | 0.59124 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1093682.3848 | 1616566.8933 | 1616566.8933 | 675366.0021 | 1093682.3848 | 1616566.8933 | 1616566.8933 | 1.05 | 2.7536 | 6.0159 | 6.0159 | 1726.6651 | 690.666 | 996.0974 | 996.0974 | 0.4 | 0.57689 | 0.57689 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1170508.8047 | 1688139.7028 | 1688139.7028 | 698699.0415 | 1170508.8047 | 1688139.7028 | 1688139.7028 | 1.05 | 2.9469 | 6.1295 | 6.1295 | 1726.5913 | 690.6365 | 970.6343 | 970.6343 | 0.4 | 0.56217 | 0.56217 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1247882.6228 | 1753799.0357 | 1753799.0357 | 721437.9097 | 1247882.6228 | 1753799.0357 | 1753799.0357 | 1.05 | 3.1415 | 6.2051 | 6.2051 | 1726.5169 | 690.6068 | 937.4638 | 937.4638 | 0.4 | 0.54298 | 0.54298 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1325815.5994 | 1799727.6747 | 1799727.6747 | 743640.4548 | 1325815.5994 | 1799727.6747 | 1799727.6747 | 1.05 | 3.3376 | 6.15 | 6.15 | 1726.442 | 690.5768 | 829.3424 | 829.3424 | 0.4 | 0.48038 | 0.48038 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1404319.8684 | 1686506.251 | 1686506.251 | 765356.7026 | 1404319.8684 | 1686506.251 | 1686506.251 | 1.05 | 3.535 | 5.0984 | 5.0984 | 1726.3665 | 690.5466 | 825.8667 | 825.8667 | 0.4 | 0.47838 | 0.47838 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1483407.9506 | 1774097.8681 | 1774097.8681 | 786630.2919 | 1483407.9506 | 1774097.8681 | 1774097.8681 | 1.05 | 3.734 | 5.3408 | 5.3408
680 | 1725.642 | 690.2568 | 1035.3852 | 1380.5136 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 278811.9726 | 418217.9589 | 557623.9451 | 341104.3218 | 0.48937 | 418217.9589 | 557623.9451 | 1.05 | 1.05 | 1.5784 | 2.8061 | 1725.5746 | 690.2298 | 1035.3447 | 1369.3571 | 0.4 | 0.6 | 0.79357 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 349527.3944 | 524291.0916 | 693432.5559 | 381927.2148 | 0.43708 | 524291.0916 | 693432.5559 | 1.05 | 1.05 | 1.9787 | 3.4613 | 1725.5067 | 690.2027 | 1035.304 | 1320.4185 | 0.4 | 0.6 | 0.76524 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 420662.0892 | 630993.1337 | 804763.5693 | 419001.1531 | 420662.0892 | 630993.1337 | 804763.5693 | 1.05 | 1.0583 | 2.3813 | 3.8734 | 1725.4385 | 690.1754 | 1035.2631 | 1276.0879 | 0.4 | 0.6 | 0.73957 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 492223.6146 | 738335.4219 | 910088.3241 | 453250.551 | 492223.6146 | 738335.4219 | 910088.3241 | 1.05 | 1.2383 | 2.7862 | 4.2333 | 1725.3699 | 690.1479 | 1035.2219 | 1235.6592 | 0.4 | 0.6 | 0.71617 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 564219.7697 | 846329.6546 | 1010194.0924 | 485277.2234 | 564219.7697 | 846329.6546 | 1010194.0924 | 1.05 | 1.4194 | 3.1937 | 4.5501 | 1725.3008 | 690.1203 | 1035.1805 | 1198.5624 | 0.4 | 0.6 | 0.6947 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 636658.6005 | 954987.9008 | 1105713.0747 | 515498.9179 | 636658.6005 | 954987.9008 | 1105713.0747 | 1.05 | 1.6016 | 3.6035 | 4.8308 | 1725.2313 | 690.0925 | 1035.1388 | 1164.3277 | 0.4 | 0.6 | 0.67488 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 709548.4059 | 1064322.6088 | 1197153.7591 | 544219.6477 | 709548.4059 | 1064322.6088 | 1197153.7591 | 1.05 | 1.7849 | 4.0159 | 5.0809 | 1725.1613 | 690.0645 | 1035.0968 | 1132.5593 | 0.4 | 0.6 | 0.65649 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 782897.7437 | 1174346.6156 | 1284920.6051 | 571668.851 | 782897.7437 | 1174346.6156 | 1284920.6051 | 1.05 | 1.9693 | 4.4309 | 5.3046 | 1725.0909 | 690.0364 | 1035.0545 | 1102.9132 | 0.4 | 0.6 | 0.63934 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 856715.4377 | 1285073.1565 | 1369323.1237 | 598024.7635 | 856715.4377 | 1285073.1565 | 1369323.1237 | 1.05 | 2.1549 | 4.8485 | 5.5051 | 1725.02 | 690.008 | 1035.012 | 1075.0753 | 0.4 | 0.6 | 0.62322 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 931010.5836 | 1396515.8754 | 1450572.2965 | 623429.146 | 931010.5836 | 1396515.8754 | 1450572.2965 | 1.05 | 2.3417 | 5.2687 | 5.6845 | 1724.9487 | 689.9795 | 1034.9692 | 1048.7355 | 0.4 | 0.6 | 0.60798 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1005792.5571 | 1508688.8357 | 1528756.2265 | 647996.9819 | 1005792.5571 | 1508688.8357 | 1528756.2265 | 1.05 | 2.5296 | 5.6917 | 5.8441 | 1724.8768 | 689.9507 | 1023.543 | 1023.543 | 0.4 | 0.5934 | 0.5934 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1081071.0207 | 1603770.5458 | 1603770.5458 | 671823.0948 | 1081071.0207 | 1603770.5458 | 1603770.5458 | 1.05 | 2.7189 | 5.9836 | 5.9836 | 1724.8045 | 689.9218 | 999.0028 | 999.0028 | 0.4 | 0.5792 | 0.5792 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1156855.932 | 1675120.6386 | 1675120.6386 | 694986.805 | 1156855.932 | 1675120.6386 | 1675120.6386 | 1.05 | 2.9093 | 6.1 | 6.1 | 1724.7317 | 689.8927 | 974.1245 | 974.1245 | 0.4 | 0.5648 | 0.5648 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1233157.5521 | 1741211.3647 | 1741211.3647 | 717555.2905 | 1233157.5521 | 1741211.3647 | 1741211.3647 | 1.05 | 3.1011 | 6.1827 | 6.1827 | 1724.6584 | 689.8634 | 944.8205 | 944.8205 | 0.4 | 0.54783 | 0.54783 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1309986.4546 | 1794126.4529 | 1794126.4529 | 739586.068 | 1309986.4546 | 1794126.4529 | 1794126.4529 | 1.05 | 3.2942 | 6.179 | 6.179 | 1724.5845 | 689.8338 | 829.0817 | 829.0817 | 0.4 | 0.48074 | 0.48074 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1387353.5347 | 1667400.6701 | 1667400.6701 | 761128.8591 | 1387353.5347 | 1667400.6701 | 1667400.6701 | 1.05 | 3.4886 | 5.0391 | 5.0391 | 1724.5102 | 689.8041 | 825.7274 | 825.7274 | 0.4 | 0.47882 | 0.47882 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1465270.0201 | 1753996.0193 | 1753996.0193 | 782227.0196 | 1465270.0201 | 1753996.0193 | 1753996.0193 | 1.05 | 3.6843 | 5.2794 | 5.2794
690 | 1723.769 | 689.5076 | 1034.2614 | 1379.0152 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 275980.3381 | 413970.5072 | 551960.6763 | 339552.0801 | 0.49214 | 413970.5072 | 551960.6763 | 1.05 | 1.05 | 1.5607 | 2.7746 | 1723.7023 | 689.4809 | 1034.2214 | 1370.203 | 0.4 | 0.6 | 0.79492 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 345942.663 | 518913.9945 | 687490.6312 | 380169.9524 | 0.43958 | 518913.9945 | 687490.6312 | 1.05 | 1.05 | 1.9563 | 3.4337 | 1723.6352 | 689.4541 | 1034.1811 | 1321.5328 | 0.4 | 0.6 | 0.76671 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 416304.9512 | 624457.4268 | 797965.5737 | 417051.7672 | 0.40072 | 624457.4268 | 797965.5737 | 1.05 | 1.05 | 2.354 | 3.8439 | 1723.5678 | 689.4271 | 1034.1407 | 1277.4275 | 0.4 | 0.6 | 0.74115 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 487074.0953 | 730611.143 | 902491.1249 | 451118.0406 | 487074.0953 | 730611.143 | 902491.1249 | 1.05 | 1.224 | 2.7541 | 4.2024 | 1723.4999 | 689.4 | 1034.0999 | 1237.1912 | 0.4 | 0.6 | 0.71784 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 558257.1999 | 837385.7999 | 1001843.5384 | 482968.0453 | 558257.1999 | 837385.7999 | 1001843.5384 | 1.05 | 1.4029 | 3.1565 | 4.5181 | 1723.4316 | 689.3726 | 1034.059 | 1200.2614 | 0.4 | 0.6 | 0.69644 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 629861.5868 | 944792.3801 | 1096647.1496 | 513017.7551 | 629861.5868 | 944792.3801 | 1096647.1496 | 1.05 | 1.5828 | 3.5612 | 4.798 | 1723.3629 | 689.3452 | 1034.0177 | 1166.1749 | 0.4 | 0.6 | 0.67669 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 701894.7994 | 1052842.1991 | 1187405.2494 | 541569.8804 | 701894.7994 | 1052842.1991 | 1187405.2494 | 1.05 | 1.7637 | 3.9683 | 5.0475 | 1723.2938 | 689.3175 | 1033.9763 | 1134.5415 | 0.4 | 0.6 | 0.65836 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 774364.6084 | 1161546.9126 | 1274519.7588 | 568852.8629 | 774364.6084 | 1161546.9126 | 1274519.7588 | 1.05 | 1.9457 | 4.3779 | 5.2709 | 1723.2242 | 689.2897 | 1033.9345 | 1105.023 | 0.4 | 0.6 | 0.64125 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 847279.0168 | 1270918.5252 | 1358300.9298 | 595044.1501 | 847279.0168 | 1270918.5252 | 1358300.9298 | 1.05 | 2.1288 | 4.7899 | 5.4712 | 1723.1542 | 689.2617 | 1033.8925 | 1077.3126 | 0.4 | 0.6 | 0.6252 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 920646.2655 | 1380969.3983 | 1438965.5312 | 620284.8614 | 920646.2655 | 1380969.3983 | 1438965.5312 | 1.05 | 2.3131 | 5.2045 | 5.6508 | 1723.0838 | 689.2335 | 1033.8503 | 1051.1108 | 0.4 | 0.6 | 0.61002 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 994474.8392 | 1491712.2588 | 1516616.8927 | 644689.4453 | 994474.8392 | 1491712.2588 | 1516616.8927 | 1.05 | 2.4985 | 5.6216 | 5.8109 | 1723.0129 | 689.2052 | 1026.0868 | 1026.0868 | 0.4 | 0.59552 | 0.59552 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1068773.4725 | 1591187.0079 | 1591187.0079 | 668352.2693 | 1068773.4725 | 1591187.0079 | 1591187.0079 | 1.05 | 2.685 | 5.9514 | 5.9514 | 1722.9416 | 689.1766 | 1001.7933 | 1001.7933 | 0.4 | 0.58144 | 0.58144 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1143551.1562 | 1662276.2003 | 1662276.2003 | 691352.2574 | 1143551.1562 | 1662276.2003 | 1662276.2003 | 1.05 | 2.8728 | 6.0701 | 6.0701 | 1722.8697 | 689.1479 | 977.3991 | 977.3991 | 0.4 | 0.56731 | 0.56731 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1218817.1445 | 1728614.0968 | 1728614.0968 | 713756.2369 | 1218817.1445 | 1728614.0968 | 1728614.0968 | 1.05 | 3.0617 | 6.1587 | 6.1587 | 1722.7974 | 689.119 | 950.1222 | 950.1222 | 0.4 | 0.5515 | 0.5515 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1294580.9615 | 1784902.3813 | 1784902.3813 | 735621.4092 | 1294580.9615 | 1784902.3813 | 1784902.3813 | 1.05 | 3.2519 | 6.1817 | 6.1817 | 1722.7246 | 689.0899 | 828.7889 | 828.7889 | 0.4 | 0.48109 | 0.48109 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1370852.4096 | 1648765.0065 | 1648765.0065 | 756997.2082 | 1370852.4096 | 1648765.0065 | 1648765.0065 | 1.05 | 3.4434 | 4.981 | 4.981 | 1722.6513 | 689.0605 | 825.5482 | 825.5482 | 0.4 | 0.47923 | 0.47923 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1447641.5769 | 1734387.3429 | 1734387.3429 | 777926.7238 | 1447641.5769 | 1734387.3429 | 1734387.3429 | 1.05 | 3.6361 | 5.2192 | 5.2192
700 | 1721.894 | 688.7576 | 1033.1364 | 1377.5152 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 273201.9346 | 409802.9019 | 546403.8692 | 338022.4469 | 0.4949 | 409802.9019 | 546403.8692 | 1.05 | 1.05 | 1.5433 | 2.7436 | 1721.828 | 688.7312 | 1033.0968 | 1371.0083 | 0.4 | 0.6 | 0.79625 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 342426.913 | 513640.3696 | 681644.9501 | 378439.0331 | 0.44207 | 513640.3696 | 681644.9501 | 1.05 | 1.05 | 1.9343 | 3.4065 | 1721.7616 | 688.7047 | 1033.057 | 1322.6034 | 0.4 | 0.6 | 0.76817 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 412033.6433 | 618050.4649 | 791278.347 | 415132.4549 | 0.40301 | 618050.4649 | 791278.347 | 1.05 | 1.05 | 2.3274 | 3.8148 | 1721.6949 | 688.678 | 1033.0169 | 1278.7207 | 0.4 | 0.6 | 0.74271 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 482028.4188 | 723042.6282 | 895018.8301 | 449019.3818 | 482028.4188 | 723042.6282 | 895018.8301 | 1.05 | 1.2101 | 2.7226 | 4.1718 | 1721.6278 | 688.6511 | 1032.9767 | 1238.6743 | 0.4 | 0.6 | 0.71948 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 552417.7201 | 828626.5802 | 993631.8122 | 480696.5798 | 552417.7201 | 828626.5802 | 993631.8122 | 1.05 | 1.3867 | 3.1201 | 4.4864 | 1721.5603 | 688.6241 | 1032.9362 | 1201.9093 | 0.4 | 0.6 | 0.69815 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 623208.2186 | 934812.3279 | 1087733.8471 | 510578.2759 | 623208.2186 | 934812.3279 | 1087733.8471 | 1.05 | 1.5643 | 3.5198 | 4.7655 | 1721.4924 | 688.5969 | 1032.8954 | 1167.9686 | 0.4 | 0.6 | 0.67846 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 694406.7806 | 1041610.1709 | 1177823.0094 | 538965.8994 | 694406.7806 | 1041610.1709 | 1177823.0094 | 1.05 | 1.743 | 3.9217 | 5.0145 | 1721.4241 | 688.5696 | 1032.8544 | 1136.4677 | 0.4 | 0.6 | 0.66019 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 766020.4716 | 1149030.7074 | 1264298.5141 | 566086.9141 | 766020.4716 | 1149030.7074 | 1264298.5141 | 1.05 | 1.9227 | 4.326 | 5.2375 | 1721.3553 | 688.5421 | 1032.8132 | 1107.0739 | 0.4 | 0.6 | 0.64314 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 838056.5608 | 1257084.8412 | 1347470.9251 | 592117.9961 | 838056.5608 | 1257084.8412 | 1347470.9251 | 1.05 | 2.1034 | 4.7326 | 5.4377 | 1721.2862 | 688.5145 | 1032.7717 | 1079.4868 | 0.4 | 0.6 | 0.62714 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 910522.5255 | 1365783.7883 | 1427561.8354 | 617199.639 | 910522.5255 | 1365783.7883 | 1427561.8354 | 1.05 | 2.2852 | 5.1416 | 5.6173 | 1721.2167 | 688.4867 | 1032.73 | 1053.4166 | 0.4 | 0.6 | 0.61202 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 983426.056 | 1475139.0841 | 1504687.5971 | 641445.7707 | 983426.056 | 1475139.0841 | 1504687.5971 | 1.05 | 2.468 | 5.5531 | 5.7778 | 1721.1467 | 688.4587 | 1028.5501 | 1028.5501 | 0.4 | 0.5976 | 0.5976 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1056775.0605 | 1578810.9894 | 1578810.9894 | 664950.3171 | 1056775.0605 | 1578810.9894 | 1578810.9894 | 1.05 | 2.652 | 5.9193 | 5.9193 | 1721.0763 | 688.4305 | 1004.4794 | 1004.4794 | 0.4 | 0.58363 | 0.58363 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1130577.6703 | 1649610.1431 | 1649610.1431 | 687791.8198 | 1130577.6703 | 1649610.1431 | 1649610.1431 | 1.05 | 2.8371 | 6.04 | 6.04 | 1721.0054 | 688.4022 | 980.4942 | 980.4942 | 0.4 | 0.56972 | 0.56972 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1204842.2455 | 1716062.0077 | 1716062.0077 | 710036.7694 | 1204842.2455 | 1716062.0077 | 1716062.0077 | 1.05 | 3.0233 | 6.1333 | 6.1333 | 1720.9341 | 688.3736 | 954.5555 | 954.5555 | 0.4 | 0.55467 | 0.55467 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1279577.3805 | 1774367.221 | 1774367.221 | 731742.0661 | 1279577.3805 | 1774367.221 | 1774367.221 | 1.05 | 3.2107 | 6.1739 | 6.1739 | 1720.8623 | 688.3449 | 828.4665 | 828.4665 | 0.4 | 0.48143 | 0.48143 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1354791.9103 | 1630577.3887 | 1630577.3887 | 752956.8708 | 1354791.9103 | 1630577.3887 | 1630577.3887 | 1.05 | 3.3993 | 4.9242 | 4.9242 | 1720.79 | 688.316 | 825.3321 | 825.3321 | 0.4 | 0.47962 | 0.47962 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1430494.9167 | 1715249.095 | 1715249.095 | 773724.0222 | 1430494.9167 | 1715249.095 | 1715249.095 | 1.05 | 3.5891 | 5.1603 | 5.1603
710 | 1720.0169 | 688.0067 | 1032.0101 | 1376.0135 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 270475.1363 | 405712.7045 | 540950.2726 | 336514.8118 | 0.49766 | 405712.7045 | 540950.2726 | 1.05 | 1.05 | 1.5262 | 2.7133 | 1719.9515 | 687.9806 | 1031.9709 | 1371.774 | 0.4 | 0.6 | 0.79757 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 338977.9499 | 508466.9249 | 675892.7812 | 376733.7077 | 0.44455 | 508466.9249 | 675892.7812 | 1.05 | 1.05 | 1.9127 | 3.3797 | 1719.8859 | 687.9544 | 1031.9315 | 1323.6313 | 0.4 | 0.6 | 0.7696 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 407845.3234 | 611767.985 | 784698.6267 | 413242.3176 | 0.40529 | 611767.985 | 784698.6267 | 1.05 | 1.05 | 2.3012 | 3.786 | 1719.8199 | 687.9279 | 1031.8919 | 1279.9688 | 0.4 | 0.6 | 0.74425 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 477083.0102 | 715624.5153 | 887667.6181 | 446953.5137 | 477083.0102 | 715624.5153 | 887667.6181 | 1.05 | 1.1963 | 2.6918 | 4.1416 | 1719.7535 | 687.9014 | 1031.8521 | 1240.11 | 0.4 | 0.6 | 0.7211 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 546696.929 | 820045.3934 | 985554.502 | 478461.59 | 546696.929 | 820045.3934 | 985554.502 | 1.05 | 1.3708 | 3.0844 | 4.4551 | 1719.6867 | 687.8747 | 1031.812 | 1203.5075 | 0.4 | 0.6 | 0.69984 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 616693.1662 | 925039.7493 | 1078968.1365 | 508179.0517 | 616693.1662 | 925039.7493 | 1078968.1365 | 1.05 | 1.5463 | 3.4792 | 4.7334 | 1719.6196 | 687.8478 | 1031.7718 | 1169.7106 | 0.4 | 0.6 | 0.68021 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 687077.98 | 1030616.9701 | 1168401.3703 | 536406.0679 | 687077.98 | 1030616.9701 | 1168401.3703 | 1.05 | 1.7227 | 3.8761 | 4.9818 | 1719.5521 | 687.8208 | 1031.7313 | 1138.3398 | 0.4 | 0.6 | 0.662 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 757857.8036 | 1136786.7055 | 1254250.5699 | 563369.1421 | 757857.8036 | 1136786.7055 | 1254250.5699 | 1.05 | 1.9001 | 4.2752 | 5.2044 | 1719.4842 | 687.7937 | 1031.6905 | 1109.0677 | 0.4 | 0.6 | 0.645 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 829039.2488 | 1243558.8731 | 1336826.2385 | 589244.194 | 829039.2488 | 1243558.8731 | 1336826.2385 | 1.05 | 2.0785 | 4.6766 | 5.4044 | 1719.4159 | 687.7664 | 1031.6495 | 1081.6002 | 0.4 | 0.6 | 0.62905 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 900629.1096 | 1350943.6644 | 1416353.9637 | 614171.1055 | 900629.1096 | 1350943.6644 | 1416353.9637 | 1.05 | 2.2579 | 5.0802 | 5.5841 | 1719.3472 | 687.7389 | 1031.6083 | 1055.6562 | 0.4 | 0.6 | 0.61399 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 972634.3666 | 1458951.5499 | 1492961.2518 | 638263.2975 | 972634.3666 | 1458951.5499 | 1492961.2518 | 1.05 | 2.4383 | 5.4862 | 5.745 | 1719.2781 | 687.7112 | 1030.9376 | 1030.9376 | 0.4 | 0.59963 | 0.59963 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1045062.1908 | 1566637.0737 | 1566637.0737 | 661614.267 | 1045062.1908 | 1566637.0737 | 1566637.0737 | 1.05 | 2.6198 | 5.8873 | 5.8873 | 1719.2086 | 687.6834 | 1007.0694 | 1007.0694 | 0.4 | 0.58578 | 0.58578 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1117919.9476 | 1637123.9193 | 1637123.9193 | 684302.1856 | 1117919.9476 | 1637123.9193 | 1637123.9193 | 1.05 | 2.8023 | 6.0098 | 6.0098 | 1719.1387 | 687.6555 | 983.4358 | 983.4358 | 0.4 | 0.57205 | 0.57205 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1191215.2017 | 1703590.9657 | 1703590.9657 | 706393.2198 | 1191215.2017 | 1703590.9657 | 1703590.9657 | 1.05 | 2.9859 | 6.107 | 6.107 | 1719.0683 | 687.6273 | 958.4702 | 958.4702 | 0.4 | 0.55755 | 0.55755 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1264955.7217 | 1763196.9982 | 1763196.9982 | 727943.981 | 1264955.7217 | 1763196.9982 | 1763196.9982 | 1.05 | 3.1706 | 6.1602 | 6.1602 | 1718.9975 | 687.599 | 828.1164 | 828.1164 | 0.4 | 0.48174 | 0.48174 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1339149.4845 | 1612817.5489 | 1612817.5489 | 749003.3696 | 1339149.4845 | 1612817.5489 | 1612817.5489 | 1.05 | 3.3564 | 4.8685 | 4.8685 | 1718.9262 | 687.5705 | 825.0819 | 825.0819 | 0.4 | 0.48 | 0.48 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1413804.6812 | 1696560.1746 | 1696560.1746 | 769613.986 | 1413804.6812 | 1696560.1746 | 1696560.1746 | 1.05 | 3.5434 | 5.1025 | 5.1025
720 | 1718.1376 | 687.255 | 1030.8826 | 1374.5101 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 267798.3908 | 401697.5862 | 535596.7816 | 335028.591 | 0.50042 | 401697.5862 | 535596.7816 | 1.05 | 1.05 | 1.5095 | 2.6835 | 1718.073 | 687.2292 | 1030.8438 | 1372.501 | 0.4 | 0.6 | 0.79886 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 335593.6837 | 503390.5256 | 670231.5167 | 375053.2621 | 0.44703 | 503390.5256 | 670231.5167 | 1.05 | 1.05 | 1.8915 | 3.3532 | 1718.008 | 687.2032 | 1030.8048 | 1324.6177 | 0.4 | 0.6 | 0.77102 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 403737.2927 | 605605.9391 | 778223.3073 | 411380.5012 | 0.40757 | 605605.9391 | 778223.3073 | 1.05 | 1.05 | 2.2755 | 3.7576 | 1717.9427 | 687.1771 | 1030.7656 | 1281.1728 | 0.4 | 0.6 | 0.74576 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 472234.4841 | 708351.7261 | 880433.8618 | 444919.4314 | 472234.4841 | 708351.7261 | 880433.8618 | 1.05 | 1.1829 | 2.6615 | 4.1117 | 1717.877 | 687.1508 | 1030.7262 | 1241.4994 | 0.4 | 0.6 | 0.72269 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 541090.6695 | 811636.0042 | 977607.4323 | 476261.9071 | 541090.6695 | 811636.0042 | 977607.4323 | 1.05 | 1.3553 | 3.0494 | 4.4241 | 1717.811 | 687.1244 | 1030.6866 | 1205.0575 | 0.4 | 0.6 | 0.70151 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 610311.4089 | 915467.1134 | 1070345.2686 | 505818.7368 | 610311.4089 | 915467.1134 | 1070345.2686 | 1.05 | 1.5286 | 3.4394 | 4.7016 | 1717.7447 | 687.0979 | 1030.6468 | 1171.4022 | 0.4 | 0.6 | 0.68194 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 679902.4134 | 1019853.6202 | 1159134.9929 | 533888.8484 | 679902.4134 | 1019853.6202 | 1159134.9929 | 1.05 | 1.7029 | 3.8315 | 4.9494 | 1717.6779 | 687.0712 | 1030.6068 | 1140.1593 | 0.4 | 0.6 | 0.66378 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 749869.548 | 1124804.322 | 1244370.0017 | 560697.8013 | 749869.548 | 1124804.322 | 1244370.0017 | 1.05 | 1.878 | 4.2256 | 5.1717 | 1717.6108 | 687.0443 | 1030.5665 | 1111.0064 | 0.4 | 0.6 | 0.64683 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 820218.8346 | 1230328.2518 | 1326360.4146 | 586420.7735 | 820218.8346 | 1230328.2518 | 1326360.4146 | 1.05 | 2.0541 | 4.6218 | 5.3715 | 1717.5433 | 687.0173 | 1030.526 | 1083.6552 | 0.4 | 0.6 | 0.63093 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 890956.4551 | 1336434.6826 | 1405335.0951 | 611197.0481 | 890956.4551 | 1336434.6826 | 1405335.0951 | 1.05 | 2.2312 | 5.0202 | 5.5512 | 1717.4755 | 686.9902 | 1030.4853 | 1057.8324 | 0.4 | 0.6 | 0.61592 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 962088.7549 | 1443133.1323 | 1481431.1132 | 635139.551 | 962088.7549 | 1443133.1323 | 1481431.1132 | 1.05 | 2.4092 | 5.4208 | 5.7123 | 1717.4072 | 686.9629 | 1030.4443 | 1033.2533 | 0.4 | 0.6 | 0.60164 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1033622.2457 | 1550433.3686 | 1554659.8188 | 658341.3616 | 1033622.2457 | 1550433.3686 | 1554659.8188 | 1.05 | 2.5883 | 5.8236 | 5.8554 | 1717.3386 | 686.9354 | 1009.5707 | 1009.5707 | 0.4 | 0.58787 | 0.58787 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1105563.6097 | 1624817.3712 | 1624817.3712 | 680880.293 | 1105563.6097 | 1624817.3712 | 1624817.3712 | 1.05 | 2.7683 | 5.9794 | 5.9794 | 1717.2695 | 686.9078 | 986.2435 | 986.2435 | 0.4 | 0.57431 | 0.57431 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1177919.7023 | 1691224.9127 | 1691224.9127 | 702822.1987 | 1177919.7023 | 1691224.9127 | 1691224.9127 | 1.05 | 2.9494 | 6.08 | 6.08 | 1717.2001 | 686.88 | 962.0269 | 962.0269 | 0.4 | 0.56023 | 0.56023 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1250697.5568 | 1751695.5293 | 1751695.5293 | 724223.4123 | 1250697.5568 | 1751695.5293 | 1751695.5293 | 1.05 | 3.1315 | 6.1427 | 6.1427 | 1717.1302 | 686.8521 | 927.5677 | 927.5677 | 0.4 | 0.54018 | 0.54018 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1323904.3876 | 1787882.7427 | 1787882.7427 | 745132.5848 | 1323904.3876 | 1787882.7427 | 1787882.7427 | 1.05 | 3.3146 | 6.0451 | 6.0451 | 1717.0599 | 686.824 | 824.8001 | 824.8001 | 0.4 | 0.48036 | 0.48036 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1397547.5951 | 1678300.965 | 1678300.965 | 765592.0895 | 1397547.5951 | 1678300.965 | 1678300.965 | 1.05 | 3.4989 | 5.0458 | 5.0458
730 | 1716.2563 | 686.5025 | 1029.7538 | 1373.005 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 265170.2142 | 397755.3212 | 530340.4283 | 333563.2254 | 0.50317 | 397755.3212 | 530340.4283 | 1.05 | 1.05 | 1.493 | 2.6543 | 1716.1923 | 686.4769 | 1029.7154 | 1372.9538 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 332272.1221 | 498408.1831 | 664544.2442 | 373397.0148 | 0.44951 | 498408.1831 | 664544.2442 | 1.05 | 1.05 | 1.8708 | 3.3258 | 1716.128 | 686.4512 | 1029.6768 | 1325.5634 | 0.4 | 0.6 | 0.77242 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 399706.9855 | 599560.4783 | 771849.429 | 409546.1929 | 0.40985 | 599560.4783 | 771849.429 | 1.05 | 1.05 | 2.2503 | 3.7295 | 1716.0634 | 686.4253 | 1029.638 | 1282.3338 | 0.4 | 0.6 | 0.74725 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 467479.6301 | 701219.4451 | 873314.1137 | 442916.181 | 467479.6301 | 701219.4451 | 873314.1137 | 1.05 | 1.1697 | 2.6318 | 4.0821 | 1715.9984 | 686.3994 | 1029.5991 | 1242.8438 | 0.4 | 0.6 | 0.72427 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 535595.0099 | 803392.5148 | 969786.6447 | 474096.4253 | 535595.0099 | 803392.5148 | 969786.6447 | 1.05 | 1.3401 | 3.0152 | 4.3935 | 1715.9331 | 686.3733 | 1029.5599 | 1206.5606 | 0.4 | 0.6 | 0.70315 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 604058.21 | 906087.3151 | 1061860.7527 | 503496.0611 | 604058.21 | 906087.3151 | 1061860.7527 | 1.05 | 1.5113 | 3.4005 | 4.6702 | 1715.8675 | 686.347 | 1029.5205 | 1173.045 | 0.4 | 0.6 | 0.68365 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 672874.4487 | 1009311.6731 | 1150018.8397 | 531412.7935 | 672874.4487 | 1009311.6731 | 1150018.8397 | 1.05 | 1.6834 | 3.7877 | 4.9174 | 1715.8015 | 686.3206 | 1029.4809 | 1141.928 | 0.4 | 0.6 | 0.66554 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 742049.0797 | 1113073.6195 | 1234651.23 | 558071.2532 | 742049.0797 | 1113073.6195 | 1234651.23 | 1.05 | 1.8564 | 4.1769 | 5.1392 | 1715.7352 | 686.2941 | 1029.4411 | 1112.8919 | 0.4 | 0.6 | 0.64864 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 811587.5948 | 1217381.3922 | 1316067.3777 | 583645.8898 | 811587.5948 | 1217381.3922 | 1316067.3777 | 1.05 | 2.0303 | 4.5682 | 5.3388 | 1715.6685 | 686.2674 | 1029.4011 | 1085.6538 | 0.4 | 0.6 | 0.63279 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 881495.6265 | 1322243.4397 | 1394498.7999 | 608275.3993 | 881495.6265 | 1322243.4397 | 1394498.7999 | 1.05 | 2.2051 | 4.9615 | 5.5186 | 1715.6015 | 686.2406 | 1029.3609 | 1059.9477 | 0.4 | 0.6 | 0.61783 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 951778.9505 | 1427668.4258 | 1470090.768 | 632072.2239 | 951778.9505 | 1427668.4258 | 1470090.768 | 1.05 | 2.3808 | 5.3569 | 5.6799 | 1715.534 | 686.2136 | 1029.3204 | 1035.5008 | 0.4 | 0.6 | 0.6036 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1022443.4886 | 1533665.233 | 1542873.8259 | 655129.036 | 1022443.4886 | 1533665.233 | 1542873.8259 | 1.05 | 2.5575 | 5.7544 | 5.8237 | 1715.4662 | 686.1865 | 1011.9893 | 1011.9893 | 0.4 | 0.58992 | 0.58992 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1093495.3114 | 1612689.2108 | 1612689.2108 | 677523.3004 | 1093495.3114 | 1612689.2108 | 1612689.2108 | 1.05 | 2.7351 | 5.949 | 5.949 | 1715.3981 | 686.1592 | 988.9324 | 988.9324 | 0.4 | 0.5765 | 0.5765 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1164940.6412 | 1678979.9416 | 1678979.9416 | 699320.5669 | 1164940.6412 | 1678979.9416 | 1678979.9416 | 1.05 | 2.9137 | 6.0524 | 6.0524 | 1715.3295 | 686.1318 | 965.3148 | 965.3148 | 0.4 | 0.56276 | 0.56276 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1236785.8554 | 1740026.7123 | 1740026.7123 | 720576.9018 | 1236785.8554 | 1740026.7123 | 1740026.7123 | 1.05 | 3.0933 | 6.1227 | 6.1227 | 1715.2606 | 686.1042 | 936.4527 | 936.4527 | 0.4 | 0.54595 | 0.54595 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1309037.4891 | 1786684.2784 | 1786684.2784 | 741340.7162 | 1309037.4891 | 1786684.2784 | 1786684.2784 | 1.05 | 3.2738 | 6.0989 | 6.0989 | 1715.1912 | 686.0765 | 824.4887 | 824.4887 | 0.4 | 0.4807 | 0.4807 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1381702.2393 | 1660453.193 | 1660453.193 | 761654.1664 | 1381702.2393 | 1660453.193 | 1660453.193 | 1.05 | 3.4554 | 4.9903 | 4.9903
740 | 1714.3728 | 685.7491 | 1028.6237 | 1371.4982 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 262589.1868 | 393883.7802 | 525178.3736 | 332118.1794 | 0.50591 | 393883.7802 | 525178.3736 | 1.05 | 1.05 | 1.4769 | 2.6255 | 1714.3095 | 685.7238 | 1028.5857 | 1371.4476 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 329011.364 | 493517.0461 | 658022.7281 | 371764.3144 | 0.45198 | 493517.0461 | 658022.7281 | 1.05 | 1.05 | 1.8504 | 3.2895 | 1714.2458 | 685.6983 | 1028.5475 | 1326.4696 | 0.4 | 0.6 | 0.77379 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 395751.9595 | 593627.9393 | 765574.1678 | 407738.6186 | 0.41212 | 593627.9393 | 765574.1678 | 1.05 | 1.05 | 2.2256 | 3.7017 | 1714.1819 | 685.6728 | 1028.5091 | 1283.453 | 0.4 | 0.6 | 0.74873 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 462815.4001 | 694223.1002 | 866305.0928 | 440942.8564 | 462815.4001 | 694223.1002 | 866305.0928 | 1.05 | 1.1568 | 2.6027 | 4.0529 | 1714.1176 | 685.6471 | 1028.4706 | 1244.1443 | 0.4 | 0.6 | 0.72582 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 530206.2263 | 795309.3394 | 962088.3817 | 471964.0969 | 530206.2263 | 795309.3394 | 962088.3817 | 1.05 | 1.3251 | 2.9816 | 4.3632 | 1714.053 | 685.6212 | 1028.4318 | 1208.0179 | 0.4 | 0.6 | 0.70477 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 597929.094 | 896893.641 | 1053510.3358 | 501209.8243 | 597929.094 | 896893.641 | 1053510.3358 | 1.05 | 1.4943 | 3.3623 | 4.639 | 1713.9881 | 685.5953 | 1028.3929 | 1174.6402 | 0.4 | 0.6 | 0.68533 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 665988.7769 | 998983.1654 | 1141048.1502 | 528976.5388 | 665988.7769 | 998983.1654 | 1141048.1502 | 1.05 | 1.6644 | 3.7448 | 4.8857 | 1713.9229 | 685.5692 | 1028.3537 | 1143.6472 | 0.4 | 0.6 | 0.66727 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 734390.1682 | 1101585.2523 | 1225088.9904 | 555487.9568 | 734390.1682 | 1101585.2523 | 1225088.9904 | 1.05 | 1.8352 | 4.1293 | 5.1071 | 1713.8573 | 685.5429 | 1028.3144 | 1114.7257 | 0.4 | 0.6 | 0.65042 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 803138.2824 | 1204707.4237 | 1305941.4005 | 580917.8115 | 803138.2824 | 1204707.4237 | 1305941.4005 | 1.05 | 2.007 | 4.5157 | 5.3065 | 1713.7914 | 685.5166 | 1028.2748 | 1087.598 | 0.4 | 0.6 | 0.63462 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 872238.2581 | 1308357.3872 | 1383839.0086 | 605404.2235 | 872238.2581 | 1308357.3872 | 1383839.0086 | 1.05 | 2.1796 | 4.904 | 5.4862 | 1713.7251 | 685.4901 | 1028.2351 | 1062.0046 | 0.4 | 0.6 | 0.61971 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 941695.3596 | 1412543.0393 | 1458934.118 | 629059.1612 | 941695.3596 | 1412543.0393 | 1458934.118 | 1.05 | 2.353 | 5.2943 | 5.6478 | 1713.6585 | 685.4634 | 1028.1951 | 1037.6833 | 0.4 | 0.6 | 0.60554 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1011514.9791 | 1517272.4687 | 1531273.7869 | 651974.8996 | 1011514.9791 | 1517272.4687 | 1531273.7869 | 1.05 | 2.5274 | 5.6866 | 5.7921 | 1713.5916 | 685.4366 | 1014.3305 | 1014.3305 | 0.4 | 0.59193 | 0.59193 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1081702.6396 | 1600737.358 | 1600737.358 | 674228.5642 | 1081702.6396 | 1600737.358 | 1600737.358 | 1.05 | 2.7027 | 5.9185 | 5.9185 | 1713.5242 | 685.4097 | 991.5147 | 991.5147 | 0.4 | 0.57864 | 0.57864 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1152263.9969 | 1666866.8102 | 1666866.8102 | 695885.4105 | 1152263.9969 | 1666866.8102 | 1666866.8102 | 1.05 | 2.8788 | 6.0244 | 6.0244 | 1713.4565 | 685.3826 | 968.3896 | 968.3896 | 0.4 | 0.56517 | 0.56517 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1223204.842 | 1728288.519 | 1728288.519 | 717001.2458 | 1223204.842 | 1728288.519 | 1728288.519 | 1.05 | 3.056 | 6.1007 | 6.1007 | 1713.3885 | 685.3554 | 941.8833 | 941.8833 | 0.4 | 0.54972 | 0.54972 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1294531.104 | 1779072.8919 | 1779072.8919 | 737624.2502 | 1294531.104 | 1779072.8919 | 1779072.8919 | 1.05 | 3.234 | 6.1081 | 6.1081 | 1713.32 | 685.328 | 824.1498 | 824.1498 | 0.4 | 0.48103 | 0.48103 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1366248.8526 | 1642999.8051 | 1642999.8051 | 757796.3718 | 1366248.8526 | 1642999.8051 | 1642999.8051 | 1.05 | 3.4131 | 4.9358 | 4.9358
750 | 1712.4872 | 684.9949 | 1027.4923 | 1369.9898 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 260053.9496 | 390080.9245 | 520107.8993 | 330692.9389 | 0.50865 | 390080.9245 | 520107.8993 | 1.05 | 1.05 | 1.461 | 2.5973 | 1712.4245 | 684.9698 | 1027.4547 | 1369.9396 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 325809.5938 | 488714.3908 | 651619.1877 | 370154.5379 | 0.45444 | 488714.3908 | 651619.1877 | 1.05 | 1.05 | 1.8303 | 3.2539 | 1712.3615 | 684.9446 | 1027.4169 | 1327.337 | 0.4 | 0.6 | 0.77515 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 391869.8878 | 587804.8317 | 759394.8259 | 405957.0396 | 0.41438 | 587804.8317 | 759394.8259 | 1.05 | 1.05 | 2.2014 | 3.6742 | 1712.2982 | 684.9193 | 1027.3789 | 1284.5312 | 0.4 | 0.6 | 0.75018 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 458238.8969 | 687358.3453 | 859403.6725 | 438998.5955 | 458238.8969 | 687358.3453 | 859403.6725 | 1.05 | 1.1441 | 2.5741 | 4.024 | 1712.2347 | 684.8939 | 1027.3408 | 1245.402 | 0.4 | 0.6 | 0.72735 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 524920.7869 | 787381.1804 | 954509.0712 | 469863.9276 | 524920.7869 | 787381.1804 | 954509.0712 | 1.05 | 1.3105 | 2.9486 | 4.3332 | 1712.1708 | 684.8683 | 1027.3025 | 1209.4307 | 0.4 | 0.6 | 0.70637 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 591919.826 | 887879.739 | 1045289.9843 | 498958.8904 | 591919.826 | 887879.739 | 1045289.9843 | 1.05 | 1.4777 | 3.3248 | 4.6082 | 1712.1066 | 684.8426 | 1027.2639 | 1176.1892 | 0.4 | 0.6 | 0.68698 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 659240.386 | 988860.5791 | 1132218.4185 | 526578.7959 | 659240.386 | 988860.5791 | 1132218.4185 | 1.05 | 1.6457 | 3.7028 | 4.8543 | 1712.0421 | 684.8168 | 1027.2252 | 1145.3183 | 0.4 | 0.6 | 0.66898 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 726886.9445 | 1090330.4167 | 1215678.3087 | 552946.4599 | 726886.9445 | 1090330.4167 | 1215678.3087 | 1.05 | 1.8145 | 4.0826 | 5.0753 | 1711.9772 | 684.7909 | 1027.1863 | 1116.5095 | 0.4 | 0.6 | 0.65218 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 794864.0859 | 1192296.1289 | 1295977.0754 | 578234.9115 | 794864.0859 | 1192296.1289 | 1295977.0754 | 1.05 | 1.9841 | 4.4643 | 5.2744 | 1711.912 | 684.7648 | 1027.1472 | 1089.4895 | 0.4 | 0.6 | 0.63642 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 863176.5038 | 1294764.7558 | 1373349.985 | 602581.7053 | 863176.5038 | 1294764.7558 | 1373349.985 | 1.05 | 2.1546 | 4.8477 | 5.4541 | 1711.8466 | 684.7386 | 1027.1079 | 1064.0053 | 0.4 | 0.6 | 0.62155 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 931829.0025 | 1397743.5038 | 1447955.3627 | 626098.3459 | 931829.0025 | 1397743.5038 | 1447955.3627 | 1.05 | 2.3258 | 5.2331 | 5.6158 | 1711.7807 | 684.7123 | 1027.0684 | 1039.8037 | 0.4 | 0.6 | 0.60744 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1000826.4988 | 1501239.7482 | 1519854.5158 | 648876.7195 | 1000826.4988 | 1501239.7482 | 1519854.5158 | 1.05 | 2.4979 | 5.6204 | 5.7606 | 1711.7146 | 684.6858 | 1016.599 | 1016.599 | 0.4 | 0.59391 | 0.59391 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1070174.0241 | 1588959.1817 | 1588959.1817 | 670993.6207 | 1070174.0241 | 1588959.1817 | 1588959.1817 | 1.05 | 2.6709 | 5.8881 | 5.8881 | 1711.6481 | 684.6592 | 994 | 994 | 0.4 | 0.58073 | 0.58073 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1139876.726 | 1654892.5586 | 1654892.5586 | 692514.0187 | 1139876.726 | 1654892.5586 | 1654892.5586 | 1.05 | 2.8448 | 5.9961 | 5.9961 | 1711.5812 | 684.6325 | 971.2891 | 971.2891 | 0.4 | 0.56748 | 0.56748 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1209939.871 | 1716543.4074 | 1716543.4074 | 713493.4696 | 1209939.871 | 1716543.4074 | 1716543.4074 | 1.05 | 3.0195 | 6.0774 | 6.0774 | 1711.514 | 684.6056 | 946.2598 | 946.2598 | 0.4 | 0.55288 | 0.55288 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1280368.8458 | 1769722.0291 | 1769722.0291 | 733979.9305 | 1280368.8458 | 1769722.0291 | 1769722.0291 | 1.05 | 3.1951 | 6.1042 | 6.1042 | 1711.4464 | 684.5786 | 823.7853 | 823.7853 | 0.4 | 0.48134 | 0.48134 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1351169.1603 | 1625924.8564 | 1625924.8564 | 754015.149 | 1351169.1603 | 1625924.8564 | 1625924.8564 | 1.05 | 3.3717 | 4.8824 | 4.8824
760 | 1710.5995 | 684.2398 | 1026.3597 | 1368.4796 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 257563.2004 | 386344.8006 | 515126.4008 | 329287.0108 | 0.51139 | 386344.8006 | 515126.4008 | 1.05 | 1.05 | 1.4454 | 2.5696 | 1710.5374 | 684.215 | 1026.3225 | 1368.4299 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 322665.0758 | 483997.6136 | 645330.1515 | 368567.089 | 0.4569 | 483997.6136 | 645330.1515 | 1.05 | 1.05 | 1.8107 | 3.219 | 1710.4751 | 684.19 | 1026.285 | 1328.1665 | 0.4 | 0.6 | 0.77649 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 388058.5509 | 582087.8264 | 753308.8232 | 404200.7504 | 0.41664 | 582087.8264 | 753308.8232 | 1.05 | 1.05 | 2.1776 | 3.647 | 1710.4124 | 684.165 | 1026.2475 | 1285.5695 | 0.4 | 0.6 | 0.75161 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 453747.363 | 680621.0445 | 852606.8702 | 437082.5771 | 453747.363 | 680621.0445 | 852606.8702 | 1.05 | 1.1316 | 2.5461 | 3.9954 | 1710.3495 | 684.1398 | 1026.2097 | 1246.6179 | 0.4 | 0.6 | 0.72887 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 519735.3384 | 779603.0076 | 947045.3132 | 467794.9724 | 519735.3384 | 779603.0076 | 947045.3132 | 1.05 | 1.2961 | 2.9163 | 4.3035 | 1710.2863 | 684.1145 | 1026.1718 | 1210.8 | 0.4 | 0.6 | 0.70795 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 586026.3937 | 879039.5906 | 1037195.867 | 496742.1821 | 586026.3937 | 879039.5906 | 1037195.867 | 1.05 | 1.4614 | 3.2881 | 4.5777 | 1710.2228 | 684.0891 | 1026.1337 | 1177.6932 | 0.4 | 0.6 | 0.68862 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 652624.5376 | 978936.8063 | 1123525.3732 | 524218.3462 | 652624.5376 | 978936.8063 | 1123525.3732 | 1.05 | 1.6274 | 3.6616 | 4.8231 | 1710.159 | 684.0636 | 1026.0954 | 1146.9428 | 0.4 | 0.6 | 0.67066 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 719533.8717 | 1079300.8075 | 1206414.4771 | 550445.3926 | 719533.8717 | 1079300.8075 | 1206414.4771 | 1.05 | 1.7942 | 4.0369 | 5.0438 | 1710.0949 | 684.0379 | 1026.0569 | 1118.2447 | 0.4 | 0.6 | 0.65391 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 786758.5923 | 1180137.8884 | 1286169.289 | 575595.6572 | 786758.5923 | 1180137.8884 | 1286169.289 | 1.05 | 1.9617 | 4.4139 | 5.2426 | 1710.0304 | 684.0122 | 1026.0183 | 1091.3301 | 0.4 | 0.6 | 0.63819 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 854302.9918 | 1281454.4877 | 1363026.3001 | 599806.139 | 854302.9918 | 1281454.4877 | 1363026.3001 | 1.05 | 2.1301 | 4.7926 | 5.4222 | 1709.9657 | 683.9863 | 1025.9794 | 1065.9516 | 0.4 | 0.6 | 0.62338 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 922171.46 | 1383257.19 | 1437148.9837 | 623187.8867 | 922171.46 | 1383257.19 | 1437148.9837 | 1.05 | 2.2992 | 5.1732 | 5.5841 | 1709.9006 | 683.9602 | 1025.9404 | 1041.8647 | 0.4 | 0.6 | 0.60931 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 990368.4858 | 1485552.7287 | 1508610.9692 | 645832.4062 | 990368.4858 | 1485552.7287 | 1508610.9692 | 1.05 | 2.4691 | 5.5555 | 5.7293 | 1709.8352 | 683.9341 | 1018.7987 | 1018.7987 | 0.4 | 0.59585 | 0.59585 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1058898.6586 | 1577351.6743 | 1577351.6743 | 667816.1686 | 1058898.6586 | 1577351.6743 | 1577351.6743 | 1.05 | 2.6399 | 5.8578 | 5.8578 | 1709.7695 | 683.9078 | 996.3964 | 996.3964 | 0.4 | 0.58277 | 0.58277 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1127766.6703 | 1643061.5857 | 1643061.5857 | 689203.8644 | 1127766.6703 | 1643061.5857 | 1643061.5857 | 1.05 | 2.8115 | 5.9676 | 5.9676 | 1709.7035 | 683.8814 | 974.0398 | 974.0398 | 0.4 | 0.56971 | 0.56971 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1196977.3162 | 1704832.9196 | 1704832.9196 | 710050.8054 | 1196977.3162 | 1704832.9196 | 1704832.9196 | 1.05 | 2.9839 | 6.053 | 6.053 | 1709.6371 | 683.8548 | 950.0578 | 950.0578 | 0.4 | 0.55571 | 0.55571 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1266535.4977 | 1759557.468 | 1759557.468 | 730404.7329 | 1266535.4977 | 1759557.468 | 1759557.468 | 1.05 | 3.1572 | 6.0935 | 6.0935 | 1709.5704 | 683.8281 | 823.3967 | 823.3967 | 0.4 | 0.48164 | 0.48164 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1336446.2233 | 1609213.4132 | 1609213.4132 | 750307.2007 | 1336446.2233 | 1609213.4132 | 1609213.4132 | 1.05 | 3.3313 | 4.8299 | 4.8299
770 | 1708.7096 | 683.4839 | 1025.2258 | 1366.9677 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 255115.6903 | 382673.5354 | 510231.3806 | 327899.9209 | 0.51412 | 382673.5354 | 510231.3806 | 1.05 | 1.05 | 1.4301 | 2.5424 | 1708.6482 | 683.4593 | 1025.1889 | 1366.9185 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 319576.149 | 479364.2236 | 639152.2981 | 367001.396 | 0.45936 | 479364.2236 | 639152.2981 | 1.05 | 1.05 | 1.7914 | 3.1847 | 1708.5865 | 683.4346 | 1025.1519 | 1328.9591 | 0.4 | 0.6 | 0.77781 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 384315.8299 | 576473.7448 | 747313.6903 | 402469.0769 | 0.41889 | 576473.7448 | 747313.6903 | 1.05 | 1.05 | 2.1542 | 3.6202 | 1708.5245 | 683.4098 | 1025.1147 | 1286.5687 | 0.4 | 0.6 | 0.75303 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 449338.1717 | 674007.2576 | 845911.837 | 435194.0182 | 449338.1717 | 674007.2576 | 845911.837 | 1.05 | 1.1194 | 2.5186 | 3.9671 | 1708.4622 | 683.3849 | 1025.0773 | 1247.7931 | 0.4 | 0.6 | 0.73036 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 514646.6926 | 771970.039 | 939693.8675 | 465756.3325 | 514646.6926 | 771970.039 | 939693.8675 | 1.05 | 1.282 | 2.8845 | 4.2741 | 1708.3996 | 683.3599 | 1025.0398 | 1212.127 | 0.4 | 0.6 | 0.70951 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 580244.9907 | 870367.4861 | 1029224.3402 | 494558.6772 | 580244.9907 | 870367.4861 | 1029224.3402 | 1.05 | 1.4454 | 3.2521 | 4.5475 | 1708.3368 | 683.3347 | 1025.0021 | 1179.1533 | 0.4 | 0.6 | 0.69023 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 646136.7454 | 969205.118 | 1114964.96 | 521894.0354 | 646136.7454 | 969205.118 | 1114964.96 | 1.05 | 1.6094 | 3.6212 | 4.7923 | 1708.2737 | 683.3095 | 1024.9642 | 1148.5219 | 0.4 | 0.6 | 0.67233 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 712325.7182 | 1068488.5773 | 1197293.0335 | 547983.46 | 712325.7182 | 1068488.5773 | 1197293.0335 | 1.05 | 1.7742 | 3.992 | 5.0125 | 1708.2103 | 683.2841 | 1024.9262 | 1119.9326 | 0.4 | 0.6 | 0.65562 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 778815.7546 | 1168223.6319 | 1276513.1989 | 572998.6037 | 778815.7546 | 1168223.6319 | 1276513.1989 | 1.05 | 1.9398 | 4.3645 | 5.2111 | 1708.1465 | 683.2586 | 1024.8879 | 1093.1213 | 0.4 | 0.6 | 0.63995 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 845610.7845 | 1268416.1767 | 1352862.81 | 597075.9188 | 845610.7845 | 1268416.1767 | 1352862.81 | 1.05 | 2.1061 | 4.7386 | 5.3906 | 1708.0825 | 683.233 | 1024.8495 | 1067.8456 | 0.4 | 0.6 | 0.62517 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 912714.8238 | 1369072.2357 | 1426509.728 | 620326.0069 | 912714.8238 | 1369072.2357 | 1426509.728 | 1.05 | 2.2731 | 5.1145 | 5.5526 | 1708.0182 | 683.2073 | 1024.8109 | 1043.8686 | 0.4 | 0.6 | 0.61116 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 980131.9758 | 1470197.9637 | 1497538.2586 | 642840.0006 | 980131.9758 | 1470197.9637 | 1497538.2586 | 1.05 | 2.4409 | 5.4921 | 5.6982 | 1707.9536 | 683.1814 | 1020.9333 | 1020.9333 | 0.4 | 0.59775 | 0.59775 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1047866.4321 | 1565911.5786 | 1565911.5786 | 664694.0546 | 1047866.4321 | 1565911.5786 | 1565911.5786 | 1.05 | 2.6095 | 5.8275 | 5.8275 | 1707.8886 | 683.1555 | 998.7107 | 998.7107 | 0.4 | 0.58476 | 0.58476 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1115922.4742 | 1631376.3862 | 1631376.3862 | 685952.5871 | 1115922.4742 | 1631376.3862 | 1631376.3862 | 1.05 | 2.7789 | 5.9389 | 5.9389 | 1707.8234 | 683.1294 | 976.6616 | 976.6616 | 0.4 | 0.57188 | 0.57188 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1184304.4747 | 1693185.4706 | 1693185.4706 | 706670.6726 | 1184304.4747 | 1693185.4706 | 1693185.4706 | 1.05 | 2.949 | 6.0279 | 6.0279 | 1707.7578 | 683.1031 | 953.473 | 953.473 | 0.4 | 0.55832 | 0.55832 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1253016.899 | 1748956.6366 | 1748956.6366 | 726895.8425 | 1253016.899 | 1748956.6366 | 1748956.6366 | 1.05 | 3.12 | 6.0786 | 6.0786 | 1707.6919 | 683.0768 | 822.9856 | 822.9856 | 0.4 | 0.48193 | 0.48193 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1322064.3062 | 1592851.4643 | 1592851.4643 | 746669.4632 | 1322064.3062 | 1592851.4643 | 1592851.4643 | 1.05 | 3.2918 | 4.7784 | 4.7784
780 | 1706.8177 | 682.7271 | 1024.0906 | 1365.4541 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 252710.2211 | 379065.3317 | 505420.4423 | 326531.2135 | 0.51685 | 379065.3317 | 505420.4423 | 1.05 | 1.05 | 1.415 | 2.5156 | 1706.7568 | 682.7027 | 1024.0541 | 1365.4054 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 316541.2235 | 474811.8352 | 633082.447 | 365456.9107 | 0.46181 | 474811.8352 | 633082.447 | 1.05 | 1.05 | 1.7724 | 3.1509 | 1706.6957 | 682.6783 | 1024.0174 | 1329.7155 | 0.4 | 0.6 | 0.77912 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 380639.6998 | 570959.5497 | 741407.0609 | 400761.3738 | 0.42115 | 570959.5497 | 741407.0609 | 1.05 | 1.05 | 2.1312 | 3.5936 | 1706.6343 | 682.6537 | 1023.9806 | 1287.5297 | 0.4 | 0.6 | 0.75443 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 445008.8179 | 667513.2269 | 839315.849 | 433332.171 | 445008.8179 | 667513.2269 | 839315.849 | 1.05 | 1.1073 | 2.4915 | 3.9391 | 1706.5727 | 682.6291 | 1023.9436 | 1248.9283 | 0.4 | 0.6 | 0.73183 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 509651.8156 | 764477.7234 | 932451.6423 | 463747.1516 | 509651.8156 | 764477.7234 | 932451.6423 | 1.05 | 1.2682 | 2.8534 | 4.245 | 1706.5108 | 682.6043 | 1023.9065 | 1213.4126 | 0.4 | 0.6 | 0.71105 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 574572.0016 | 861858.0024 | 1021371.9344 | 492407.4039 | 574572.0016 | 861858.0024 | 1021371.9344 | 1.05 | 1.4296 | 3.2167 | 4.5176 | 1706.4486 | 682.5794 | 1023.8692 | 1180.5706 | 0.4 | 0.6 | 0.69183 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 639772.7567 | 959659.1351 | 1106533.3247 | 519604.7689 | 639772.7567 | 959659.1351 | 1106533.3247 | 1.05 | 1.5918 | 3.5816 | 4.7618 | 1706.3861 | 682.5545 | 1023.8317 | 1150.0566 | 0.4 | 0.6 | 0.67397 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 705257.5345 | 1057886.3018 | 1188309.7428 | 545559.4362 | 705257.5345 | 1057886.3018 | 1188309.7428 | 1.05 | 1.7547 | 3.9481 | 4.9815 | 1706.3234 | 682.5294 | 1023.794 | 1121.5747 | 0.4 | 0.6 | 0.6573 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 771029.8625 | 1156544.7937 | 1267004.2131 | 570442.3857 | 771029.8625 | 1156544.7937 | 1267004.2131 | 1.05 | 1.9183 | 4.3161 | 5.1799 | 1706.2604 | 682.5042 | 1023.7562 | 1094.8646 | 0.4 | 0.6 | 0.64167 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 837093.3429 | 1255640.0144 | 1342854.6339 | 594389.5313 | 837093.3429 | 1255640.0144 | 1342854.6339 | 1.05 | 2.0825 | 4.6857 | 5.3593 | 1706.1971 | 682.4788 | 1023.7182 | 1069.689 | 0.4 | 0.6 | 0.62694 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 903451.654 | 1355177.481 | 1416032.5924 | 617511.0347 | 903451.654 | 1355177.481 | 1416032.5924 | 1.05 | 2.2476 | 5.057 | 5.5214 | 1706.1335 | 682.4534 | 1023.6801 | 1045.8178 | 0.4 | 0.6 | 0.61298 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 970108.5507 | 1455162.826 | 1486631.6572 | 639897.6626 | 970108.5507 | 1455162.826 | 1486631.6572 | 1.05 | 2.4133 | 5.4299 | 5.6673 | 1706.0696 | 682.4278 | 1023.0059 | 1023.0059 | 0.4 | 0.59963 | 0.59963 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1037067.866 | 1554635.481 | 1554635.481 | 661625.2597 | 1037067.866 | 1554635.481 | 1554635.481 | 1.05 | 2.5798 | 5.7973 | 5.7973 | 1706.0054 | 682.4022 | 1000.9485 | 1000.9485 | 0.4 | 0.58672 | 0.58672 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1104333.5119 | 1619838.0668 | 1619838.0668 | 682757.978 | 1104333.5119 | 1619838.0668 | 1619838.0668 | 1.05 | 2.747 | 5.9102 | 5.9102 | 1705.9409 | 682.3764 | 979.1698 | 979.1698 | 0.4 | 0.57398 | 0.57398 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1171909.4805 | 1681620.8381 | 1681620.8381 | 703350.6603 | 1171909.4805 | 1681620.8381 | 1681620.8381 | 1.05 | 2.915 | 6.0021 | 6.0021 | 1705.8761 | 682.3505 | 956.6086 | 956.6086 | 0.4 | 0.56077 | 0.56077 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1239799.8451 | 1738114.4684 | 1738114.4684 | 723450.634 | 1239799.8451 | 1738114.4684 | 1738114.4684 | 1.05 | 3.0837 | 6.0608 | 6.0608 | 1705.8111 | 682.3244 | 927.5561 | 927.5561 | 0.4 | 0.54376 | 0.54376 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1308008.7615 | 1778115.3897 | 1778115.3897 | 743099.0838 | 1308008.7615 | 1778115.3897 | 1778115.3897 | 1.05 | 3.2532 | 6.012 | 6.012
790 | 1704.9235 | 681.9694 | 1022.9541 | 1363.9388 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 250345.6425 | 375518.4637 | 500691.285 | 325180.4501 | 0.51957 | 375518.4637 | 500691.285 | 1.05 | 1.05 | 1.4002 | 2.4893 | 1704.8633 | 681.9453 | 1022.918 | 1363.8906 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 313558.7751 | 470338.1627 | 627117.5503 | 363933.1067 | 0.46426 | 470338.1627 | 627117.5503 | 1.05 | 1.05 | 1.7537 | 3.1178 | 1704.8028 | 681.9211 | 1022.8817 | 1330.4364 | 0.4 | 0.6 | 0.7804 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 377028.2243 | 565542.3364 | 735586.6655 | 399077.023 | 0.42339 | 565542.3364 | 735586.6655 | 1.05 | 1.05 | 2.1087 | 3.5673 | 1704.742 | 681.8968 | 1022.8452 | 1288.4535 | 0.4 | 0.6 | 0.75581 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 440756.9105 | 661135.3657 | 832816.299 | 431496.3211 | 440756.9105 | 661135.3657 | 832816.299 | 1.05 | 1.0956 | 2.465 | 3.9114 | 1704.681 | 681.8724 | 1022.8086 | 1250.0247 | 0.4 | 0.6 | 0.73329 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 504747.8166 | 757121.7249 | 925315.6842 | 461766.613 | 504747.8166 | 757121.7249 | 925315.6842 | 1.05 | 1.2546 | 2.8228 | 4.2162 | 1704.6197 | 681.8479 | 1022.7718 | 1214.6578 | 0.4 | 0.6 | 0.71257 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 569003.9883 | 853505.9824 | 1013635.3414 | 490287.4371 | 569003.9883 | 853505.9824 | 1013635.3414 | 1.05 | 1.4142 | 3.182 | 4.488 | 1704.5582 | 681.8233 | 1022.7349 | 1181.9461 | 0.4 | 0.6 | 0.6934 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 633528.5352 | 950292.8027 | 1098226.7993 | 517349.5068 | 633528.5352 | 950292.8027 | 1098226.7993 | 1.05 | 1.5745 | 3.5427 | 4.7316 | 1704.4964 | 681.7985 | 1022.6978 | 1151.5483 | 0.4 | 0.6 | 0.67559 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 698324.6312 | 1047486.9468 | 1179460.58 | 543172.1596 | 698324.6312 | 1047486.9468 | 1179460.58 | 1.05 | 1.7355 | 3.9049 | 4.9509 | 1704.4343 | 681.7737 | 1022.6606 | 1123.1721 | 0.4 | 0.6 | 0.65897 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 763395.5158 | 1145093.2737 | 1257637.9712 | 567925.7117 | 763395.5158 | 1145093.2737 | 1257637.9712 | 1.05 | 1.8972 | 4.2686 | 5.1489 | 1704.372 | 681.7488 | 1022.6232 | 1096.5613 | 0.4 | 0.6 | 0.64338 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 828744.4945 | 1243116.7418 | 1332997.1361 | 591745.5469 | 828744.4945 | 1243116.7418 | 1332997.1361 | 1.05 | 2.0595 | 4.6339 | 5.3282 | 1704.3094 | 681.7237 | 1022.5856 | 1071.4833 | 0.4 | 0.6 | 0.62869 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 894374.9398 | 1341562.4097 | 1405712.8085 | 614741.3945 | 894374.9398 | 1341562.4097 | 1405712.8085 | 1.05 | 2.2225 | 5.0006 | 5.4903 | 1704.2465 | 681.6986 | 1022.5479 | 1047.7142 | 0.4 | 0.6 | 0.61477 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 960290.292 | 1440435.438 | 1475886.6023 | 637003.6611 | 960290.292 | 1440435.438 | 1475886.6023 | 1.05 | 2.3862 | 5.369 | 5.6365 | 1704.1833 | 681.6733 | 1022.51 | 1025.0194 | 0.4 | 0.6 | 0.60147 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1026494.0602 | 1539741.0903 | 1543519.8794 | 658607.8878 | 1026494.0602 | 1539741.0903 | 1543519.8794 | 1.05 | 2.5506 | 5.7389 | 5.7671 | 1704.1199 | 681.6479 | 1003.1149 | 1003.1149 | 0.4 | 0.58864 | 0.58864 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1092989.8229 | 1608446.715 | 1608446.715 | 679617.9659 | 1092989.8229 | 1608446.715 | 1608446.715 | 1.05 | 2.7158 | 5.8813 | 5.8813 | 1704.0561 | 681.6225 | 981.5763 | 981.5763 | 0.4 | 0.57602 | 0.57602 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1159781.2292 | 1670152.9061 | 1670152.9061 | 700088.5119 | 1159781.2292 | 1670152.9061 | 1670152.9061 | 1.05 | 2.8816 | 5.9758 | 5.9758 | 1703.9921 | 681.5968 | 959.5269 | 959.5269 | 0.4 | 0.56311 | 0.56311 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1226871.9996 | 1727145.1008 | 1727145.1008 | 720066.6544 | 1226871.9996 | 1727145.1008 | 1727145.1008 | 1.05 | 3.0482 | 6.0409 | 6.0409 | 1703.9278 | 681.5711 | 933.451 | 933.451 | 0.4 | 0.54782 | 0.54782 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1294265.927 | 1772571.9982 | 1772571.9982 | 739593.4014 | 1294265.927 | 1772571.9982 | 1772571.9982 | 1.05 | 3.2155 | 6.0313 | 6.0313
800 | 1703.0272 | 681.2109 | 1021.8163 | 1362.4218 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 248020.8488 | 372031.2733 | 496041.6977 | 323847.2084 | 0.52229 | 372031.2733 | 496041.6977 | 1.05 | 1.05 | 1.3857 | 2.4635 | 1702.9676 | 681.187 | 1021.7805 | 1362.3741 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 310627.3426 | 465941.0139 | 621254.6852 | 362429.4782 | 0.46671 | 465941.0139 | 621254.6852 | 1.05 | 1.05 | 1.7354 | 3.0852 | 1702.9076 | 681.1631 | 1021.7446 | 1331.1226 | 0.4 | 0.6 | 0.78168 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 373479.5495 | 560219.3242 | 729850.3259 | 397415.432 | 0.42564 | 560219.3242 | 729850.3259 | 1.05 | 1.05 | 2.0865 | 3.5413 | 1702.8475 | 681.139 | 1021.7085 | 1289.3406 | 0.4 | 0.6 | 0.75717 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 436580.1647 | 654870.2471 | 826410.6895 | 429685.7847 | 436580.1647 | 654870.2471 | 826410.6895 | 1.05 | 1.084 | 2.4389 | 3.884 | 1702.7871 | 681.1148 | 1021.6722 | 1251.0829 | 0.4 | 0.6 | 0.73473 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 499931.9387 | 749897.9081 | 918283.1693 | 459813.9372 | 499931.9387 | 749897.9081 | 918283.1693 | 1.05 | 1.2412 | 2.7927 | 4.1877 | 1702.7264 | 681.0906 | 1021.6359 | 1215.8635 | 0.4 | 0.6 | 0.71407 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 563537.6779 | 845306.5168 | 1006011.4036 | 488197.8959 | 563537.6779 | 845306.5168 | 1006011.4036 | 1.05 | 1.3991 | 3.1479 | 4.4586 | 1702.6655 | 681.0662 | 1021.5993 | 1183.2808 | 0.4 | 0.6 | 0.69496 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 627400.245 | 941100.3675 | 1090041.8882 | 515127.2604 | 627400.245 | 941100.3675 | 1090041.8882 | 1.05 | 1.5576 | 3.5045 | 4.7016 | 1702.6044 | 681.0417 | 1021.5626 | 1152.9978 | 0.4 | 0.6 | 0.6772 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 691522.5601 | 1037283.8402 | 1170741.7148 | 540820.5273 | 691522.5601 | 1037283.8402 | 1170741.7148 | 1.05 | 1.7167 | 3.8626 | 4.9205 | 1702.5429 | 681.0172 | 1021.5258 | 1124.7259 | 0.4 | 0.6 | 0.66062 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 755907.6011 | 1133861.4016 | 1248410.3274 | 565447.3581 | 755907.6011 | 1133861.4016 | 1248410.3274 | 1.05 | 1.8765 | 4.2221 | 5.1182 | 1702.4813 | 680.9925 | 1021.4888 | 1098.2129 | 0.4 | 0.6 | 0.64507 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 820558.4043 | 1230837.6065 | 1323285.9076 | 589142.6142 | 820558.4043 | 1230837.6065 | 1323285.9076 | 1.05 | 2.0369 | 4.583 | 5.2973 | 1702.4194 | 680.9677 | 1021.4516 | 1073.2301 | 0.4 | 0.6 | 0.63041 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 885478.0654 | 1328217.0981 | 1395545.8286 | 612015.5986 | 885478.0654 | 1328217.0981 | 1395545.8286 | 1.05 | 2.198 | 4.9454 | 5.4595 | 1702.3572 | 680.9429 | 1021.4143 | 1049.5597 | 0.4 | 0.6 | 0.61653 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 950669.7397 | 1426004.6096 | 1465298.6953 | 634156.3648 | 950669.7397 | 1426004.6096 | 1465298.6953 | 1.05 | 2.3597 | 5.3093 | 5.6059 | 1702.2947 | 680.9179 | 1021.3768 | 1026.9764 | 0.4 | 0.6 | 0.60329 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1016136.6434 | 1524204.9651 | 1532561.2346 | 655640.1551 | 1016136.6434 | 1524204.9651 | 1532561.2346 | 1.05 | 2.5221 | 5.6747 | 5.7371 | 1702.232 | 680.8928 | 1005.2141 | 1005.2141 | 0.4 | 0.59053 | 0.59053 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1081882.0539 | 1597201.6669 | 1597201.6669 | 676530.6056 | 1081882.0539 | 1597201.6669 | 1597201.6669 | 1.05 | 2.6852 | 5.8524 | 5.8524 | 1702.169 | 680.8676 | 983.8907 | 983.8907 | 0.4 | 0.57802 | 0.57802 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1147909.3105 | 1658791.4221 | 1658791.4221 | 696882.1114 | 1147909.3105 | 1658791.4221 | 1658791.4221 | 1.05 | 2.849 | 5.9491 | 5.9491 | 1702.1057 | 680.8423 | 962.2686 | 962.2686 | 0.4 | 0.56534 | 0.56534 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1214221.8156 | 1716120.7367 | 1716120.7367 | 716741.6069 | 1214221.8156 | 1716120.7367 | 1716120.7367 | 1.05 | 3.0134 | 6.0195 | 6.0195 | 1702.0421 | 680.8168 | 937.896 | 937.896 | 0.4 | 0.55104 | 0.55104 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1280823.035 | 1764466.8211 | 1764466.8211 | 736149.9283 | 1280823.035 | 1764466.8211 | 1764466.8211 | 1.05 | 3.1786 | 6.0323 | 6.0323
810 | 1700.8119 | 680.3248 | 1020.4871 | 1360.6495 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 245688.9955 | 368533.4932 | 491377.991 | 322531.0813 | 0.5251 | 368533.4932 | 491377.991 | 1.05 | 1.05 | 1.3709 | 2.4371 | 1700.7528 | 680.3011 | 1020.4517 | 1360.6022 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 307688.1884 | 461532.2825 | 615376.3767 | 360945.5391 | 0.46924 | 461532.2825 | 615376.3767 | 1.05 | 1.05 | 1.7168 | 3.052 | 1700.6934 | 680.2774 | 1020.4161 | 1331.5268 | 0.4 | 0.6 | 0.78293 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 369922.9678 | 554884.4517 | 724061.0271 | 395776.0324 | 0.42796 | 554884.4517 | 724061.0271 | 1.05 | 1.05 | 2.0639 | 3.5143 | 1700.6339 | 680.2536 | 1020.3803 | 1289.9517 | 0.4 | 0.6 | 0.75851 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 432395.8227 | 648593.7341 | 819943.8361 | 427899.9073 | 432395.8227 | 648593.7341 | 819943.8361 | 1.05 | 1.0722 | 2.4124 | 3.8554 | 1700.5741 | 680.2296 | 1020.3445 | 1251.8705 | 0.4 | 0.6 | 0.73615 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 495109.2911 | 742663.9367 | 911181.6037 | 457888.3788 | 495109.2911 | 742663.9367 | 911181.6037 | 1.05 | 1.2276 | 2.7622 | 4.158 | 1700.514 | 680.2056 | 1020.3084 | 1216.8038 | 0.4 | 0.6 | 0.71555 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 558065.9607 | 837098.9411 | 998311.0775 | 486137.9395 | 558065.9607 | 837098.9411 | 998311.0775 | 1.05 | 1.3837 | 3.1133 | 4.4279 | 1700.4538 | 680.1815 | 1020.2723 | 1184.3551 | 0.4 | 0.6 | 0.69649 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 621268.4692 | 931902.7038 | 1081773.6778 | 512937.0883 | 621268.4692 | 931902.7038 | 1081773.6778 | 1.05 | 1.5404 | 3.4658 | 4.6702 | 1700.3933 | 680.1573 | 1020.236 | 1154.1912 | 0.4 | 0.6 | 0.67878 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 684719.5051 | 1027079.2576 | 1161932.982 | 538503.4914 | 684719.5051 | 1027079.2576 | 1161932.982 | 1.05 | 1.6976 | 3.8196 | 4.8885 | 1700.3325 | 680.133 | 1020.1995 | 1126.0276 | 0.4 | 0.6 | 0.66224 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 748421.808 | 1122632.712 | 1239086.4422 | 563006.1641 | 748421.808 | 1122632.712 | 1239086.4422 | 1.05 | 1.8555 | 4.1748 | 5.0859 | 1700.2715 | 680.1086 | 1020.1629 | 1099.6155 | 0.4 | 0.6 | 0.64673 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 812378.1694 | 1218567.2542 | 1313471.997 | 586579.4528 | 812378.1694 | 1218567.2542 | 1313471.997 | 1.05 | 2.014 | 4.5314 | 5.2647 | 1700.2102 | 680.0841 | 1020.1261 | 1074.7305 | 0.4 | 0.6 | 0.63212 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 876591.4332 | 1314887.1498 | 1385269.1795 | 609332.241 | 876591.4332 | 1314887.1498 | 1385269.1795 | 1.05 | 2.1731 | 4.8894 | 5.4269 | 1700.1487 | 680.0595 | 1020.0892 | 1051.1602 | 0.4 | 0.6 | 0.61828 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 941064.4959 | 1411596.7439 | 1454592.6485 | 631354.2339 | 941064.4959 | 1411596.7439 | 1454592.6485 | 1.05 | 2.3328 | 5.2489 | 5.5735 | 1700.087 | 680.0348 | 1020.0522 | 1028.6875 | 0.4 | 0.6 | 0.60508 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1005800.3079 | 1508700.4619 | 1521472.4936 | 652720.3807 | 1005800.3079 | 1508700.4619 | 1521472.4936 | 1.05 | 2.4932 | 5.6097 | 5.7051 | 1700.025 | 680.01 | 1007.0622 | 1007.0622 | 0.4 | 0.59238 | 0.59238 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1070801.8734 | 1585806.2028 | 1585806.2028 | 673494.067 | 1070801.8734 | 1585806.2028 | 1585806.2028 | 1.05 | 2.6542 | 5.8213 | 5.8213 | 1699.9627 | 679.9851 | 985.9373 | 985.9373 | 0.4 | 0.57998 | 0.57998 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1136072.2514 | 1647236.2153 | 1647236.2153 | 693729.4711 | 1136072.2514 | 1647236.2153 | 1647236.2153 | 1.05 | 2.8159 | 5.92 | 5.92 | 1699.9001 | 679.9601 | 964.6826 | 964.6826 | 0.4 | 0.56749 | 0.56749 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1201614.5561 | 1704771.7868 | 1704771.7868 | 713473.3377 | 1201614.5561 | 1704771.7868 | 1704771.7868 | 1.05 | 2.9783 | 5.9947 | 5.9947 | 1699.8373 | 679.9349 | 941.4762 | 941.4762 | 0.4 | 0.55386 | 0.55386 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1267431.9578 | 1754957.7164 | 1754957.7164 | 732766.3349 | 1267431.9578 | 1754957.7164 | 1754957.7164 | 1.05 | 3.1413 | 6.0227 | 6.0227
820 | 1698.5936 | 679.4374 | 1019.1562 | 1358.8749 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 243395.4681 | 365093.2021 | 486790.9362 | 321231.6767 | 0.52792 | 365093.2021 | 486790.9362 | 1.05 | 1.05 | 1.3563 | 2.4112 | 1698.5351 | 679.414 | 1019.121 | 1358.828 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 304798.0912 | 457197.1368 | 609596.1824 | 359480.8215 | 0.47176 | 457197.1368 | 609596.1824 | 1.05 | 1.05 | 1.6984 | 3.0194 | 1698.4763 | 679.3905 | 1019.0858 | 1331.8963 | 0.4 | 0.6 | 0.78417 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 366426.6673 | 549640.0009 | 718353.1316 | 394158.2781 | 0.43027 | 549640.0009 | 718353.1316 | 1.05 | 1.05 | 2.0418 | 3.4876 | 1698.4173 | 679.3669 | 1019.0504 | 1290.5262 | 0.4 | 0.6 | 0.75984 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 428283.4967 | 642425.245 | 813567.8409 | 426138.0614 | 428283.4967 | 642425.245 | 813567.8409 | 1.05 | 1.0606 | 2.3863 | 3.8272 | 1698.3581 | 679.3432 | 1019.0149 | 1252.6202 | 0.4 | 0.6 | 0.73755 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 490370.9235 | 735556.3853 | 904179.9478 | 455989.2251 | 490370.9235 | 735556.3853 | 904179.9478 | 1.05 | 1.2143 | 2.7322 | 4.1285 | 1698.2987 | 679.3195 | 1018.9792 | 1217.705 | 0.4 | 0.6 | 0.71701 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 552691.3359 | 829037.0038 | 990719.4015 | 484106.7652 | 552691.3359 | 829037.0038 | 990719.4015 | 1.05 | 1.3686 | 3.0793 | 4.3975 | 1698.239 | 679.2956 | 1018.9434 | 1185.3888 | 0.4 | 0.6 | 0.69801 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 615247.1663 | 922870.7495 | 1073622.5906 | 510778.0931 | 615247.1663 | 922870.7495 | 1073622.5906 | 1.05 | 1.5234 | 3.4277 | 4.639 | 1698.1792 | 679.2717 | 1018.9075 | 1155.3429 | 0.4 | 0.6 | 0.68034 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 678040.8925 | 1017061.3387 | 1153249.5687 | 536220.0545 | 678040.8925 | 1017061.3387 | 1153249.5687 | 1.05 | 1.6789 | 3.7774 | 4.8568 | 1698.119 | 679.2476 | 1018.8714 | 1127.2863 | 0.4 | 0.6 | 0.66384 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 741075.0373 | 1111612.5559 | 1229895.7163 | 560601.0271 | 741075.0373 | 1111612.5559 | 1229895.7163 | 1.05 | 1.8349 | 4.1285 | 5.0538 | 1698.0587 | 679.2235 | 1018.8352 | 1100.9737 | 0.4 | 0.6 | 0.64837 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 804352.1695 | 1206528.2543 | 1303798.5371 | 584054.849 | 804352.1695 | 1206528.2543 | 1303798.5371 | 1.05 | 1.9915 | 4.4808 | 5.2324 | 1697.9981 | 679.1992 | 1018.7988 | 1076.1846 | 0.4 | 0.6 | 0.6338 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 867874.9043 | 1301812.3564 | 1375139.3307 | 606689.9899 | 867874.9043 | 1301812.3564 | 1375139.3307 | 1.05 | 2.1487 | 4.8345 | 5.3945 | 1697.9372 | 679.1749 | 1018.7623 | 1052.7115 | 0.4 | 0.6 | 0.61999 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 931645.9035 | 1397468.8553 | 1444038.0096 | 628595.8127 | 931645.9035 | 1397468.8553 | 1444038.0096 | 1.05 | 2.3065 | 5.1896 | 5.5412 | 1697.8762 | 679.1505 | 1018.7257 | 1030.345 | 0.4 | 0.6 | 0.60684 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 995667.8763 | 1493501.8145 | 1510536.312 | 649846.9782 | 995667.8763 | 1493501.8145 | 1510536.312 | 1.05 | 2.4649 | 5.546 | 5.6732 | 1697.8148 | 679.1259 | 1008.8484 | 1008.8484 | 0.4 | 0.5942 | 0.5942 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1059943.5796 | 1574556.9097 | 1574556.9097 | 670506.6257 | 1059943.5796 | 1574556.9097 | 1574556.9097 | 1.05 | 2.6239 | 5.7903 | 5.7903 | 1697.7533 | 679.1013 | 987.9047 | 987.9047 | 0.4 | 0.58189 | 0.58189 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1124475.8184 | 1635801.5641 | 1635801.5641 | 690628.721 | 1124475.8184 | 1635801.5641 | 1635801.5641 | 1.05 | 2.7836 | 5.8906 | 5.8906 | 1697.6914 | 679.0766 | 966.9678 | 966.9678 | 0.4 | 0.56958 | 0.56958 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1189267.4466 | 1693451.7127 | 1693451.7127 | 710259.8231 | 1189267.4466 | 1693451.7127 | 1693451.7127 | 1.05 | 2.9438 | 5.969 | 5.969 | 1697.6293 | 679.0517 | 944.6263 | 944.6263 | 0.4 | 0.55644 | 0.55644 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1254321.3672 | 1744881.7808 | 1744881.7808 | 729440.436 | 1254321.3672 | 1744881.7808 | 1744881.7808 | 1.05 | 3.1048 | 6.0082 | 6.0082
830 | 1696.3724 | 678.5489 | 1017.8234 | 1357.0979 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 241139.2664 | 361708.8996 | 482278.5328 | 319948.6159 | 0.53073 | 361708.8996 | 482278.5328 | 1.05 | 1.05 | 1.342 | 2.3857 | 1696.3144 | 678.5258 | 1017.7886 | 1357.0515 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 301955.7361 | 452933.6041 | 603911.4721 | 358034.8748 | 0.47429 | 452933.6041 | 603911.4721 | 1.05 | 1.05 | 1.6804 | 2.9873 | 1696.2562 | 678.5025 | 1017.7537 | 1332.2317 | 0.4 | 0.6 | 0.7854 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 362988.989 | 544483.4835 | 712724.6703 | 392561.6443 | 0.43259 | 544483.4835 | 712724.6703 | 1.05 | 1.05 | 2.02 | 3.4611 | 1696.1978 | 678.4791 | 1017.7187 | 1291.0651 | 0.4 | 0.6 | 0.76115 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 424241.1531 | 636361.7296 | 807280.4586 | 424399.6451 | 0.40015 | 636361.7296 | 807280.4586 | 1.05 | 1.05 | 2.3607 | 3.7992 | 1696.1392 | 678.4557 | 1017.6835 | 1253.3328 | 0.4 | 0.6 | 0.73893 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 485714.3951 | 728571.5926 | 897275.6766 | 454115.7934 | 485714.3951 | 728571.5926 | 897275.6766 | 1.05 | 1.2012 | 2.7027 | 4.0993 | 1696.0803 | 678.4321 | 1017.6482 | 1218.5677 | 0.4 | 0.6 | 0.71846 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 547410.9208 | 821116.3812 | 983233.5673 | 482103.6057 | 547410.9208 | 821116.3812 | 983233.5673 | 1.05 | 1.3537 | 3.0459 | 4.3674 | 1696.0213 | 678.4085 | 1017.6128 | 1186.383 | 0.4 | 0.6 | 0.69951 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 609332.9757 | 913999.4636 | 1065585.5326 | 508649.4184 | 609332.9757 | 913999.4636 | 1065585.5326 | 1.05 | 1.5068 | 3.3903 | 4.6082 | 1695.962 | 678.3848 | 1017.5772 | 1156.454 | 0.4 | 0.6 | 0.68189 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 671482.845 | 1007224.2676 | 1144688.0987 | 533969.2667 | 671482.845 | 1007224.2676 | 1144688.0987 | 1.05 | 1.6605 | 3.736 | 4.8254 | 1695.9025 | 678.361 | 1017.5415 | 1128.5031 | 0.4 | 0.6 | 0.66543 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 733862.8543 | 1100794.2815 | 1220834.5052 | 558230.8983 | 733862.8543 | 1100794.2815 | 1220834.5052 | 1.05 | 1.8146 | 4.0829 | 5.022 | 1695.8428 | 678.3371 | 1017.5057 | 1102.2886 | 0.4 | 0.6 | 0.64999 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 796475.3697 | 1194713.0545 | 1294261.6521 | 581567.6498 | 796475.3697 | 1194713.0545 | 1294261.6521 | 1.05 | 1.9694 | 4.4311 | 5.2004 | 1695.7828 | 678.3131 | 1017.4697 | 1077.5936 | 0.4 | 0.6 | 0.63545 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 859322.7983 | 1288984.1974 | 1365152.2578 | 604087.5833 | 859322.7983 | 1288984.1974 | 1365152.2578 | 1.05 | 2.1247 | 4.7806 | 5.3623 | 1695.7227 | 678.2891 | 1017.4336 | 1054.2152 | 0.4 | 0.6 | 0.62169 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 922407.5886 | 1383611.3829 | 1433630.7893 | 625879.7237 | 922407.5886 | 1383611.3829 | 1433630.7893 | 1.05 | 2.2806 | 5.1314 | 5.5091 | 1695.6623 | 678.2649 | 1017.3974 | 1031.9509 | 0.4 | 0.6 | 0.60858 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 985732.2309 | 1478598.3463 | 1499749.1599 | 647018.4481 | 985732.2309 | 1478598.3463 | 1499749.1599 | 1.05 | 2.4371 | 5.4835 | 5.6415 | 1695.6016 | 678.2406 | 1010.5759 | 1010.5759 | 0.4 | 0.596 | 0.596 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1049299.2576 | 1563451.8025 | 1563451.8025 | 667566.6541 | 1049299.2576 | 1563451.8025 | 1563451.8025 | 1.05 | 2.5942 | 5.7593 | 5.7593 | 1695.5407 | 678.2163 | 989.7985 | 989.7985 | 0.4 | 0.58377 | 0.58377 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1113111.2438 | 1624490.4165 | 1624490.4165 | 687578.0987 | 1113111.2438 | 1624490.4165 | 1624490.4165 | 1.05 | 2.7518 | 5.8611 | 5.8611 | 1695.4796 | 678.1918 | 969.1401 | 969.1401 | 0.4 | 0.5716 | 0.5716 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1177170.8072 | 1682183.9446 | 1682183.9446 | 707099.1587 | 1177170.8072 | 1682183.9446 | 1682183.9446 | 1.05 | 2.9101 | 5.9426 | 5.9426 | 1695.4182 | 678.1673 | 947.4732 | 947.4732 | 0.4 | 0.55884 | 0.55884 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1241480.6093 | 1734483.0099 | 1734483.0099 | 726170.1779 | 1241480.6093 | 1734483.0099 | 1734483.0099 | 1.05 | 3.069 | 5.9904 | 5.9904
840 | 1694.1482 | 677.6593 | 1016.4889 | 1355.3185 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 238919.4271 | 358379.1407 | 477838.8542 | 318681.5337 | 0.53354 | 358379.1407 | 477838.8542 | 1.05 | 1.05 | 1.3279 | 2.3607 | 1694.0907 | 677.6363 | 1016.4544 | 1355.2726 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 299159.8584 | 448739.7876 | 598319.7169 | 356607.265 | 0.47681 | 448739.7876 | 598319.7169 | 1.05 | 1.05 | 1.6626 | 2.9558 | 1694.0331 | 677.6132 | 1016.4199 | 1332.5339 | 0.4 | 0.6 | 0.7866 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 359608.3402 | 539412.5103 | 707173.7468 | 390985.6265 | 0.4349 | 539412.5103 | 707173.7468 | 1.05 | 1.05 | 1.9985 | 3.4349 | 1693.9753 | 677.5901 | 1016.3852 | 1291.5689 | 0.4 | 0.6 | 0.76245 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 420266.8424 | 630400.2637 | 801079.5303 | 422684.0804 | 0.4023 | 630400.2637 | 801079.5303 | 1.05 | 1.05 | 2.3356 | 3.7715 | 1693.9172 | 677.5669 | 1016.3503 | 1254.0089 | 0.4 | 0.6 | 0.7403 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 481137.3695 | 721706.0543 | 890466.3661 | 452267.4295 | 481137.3695 | 721706.0543 | 890466.3661 | 1.05 | 1.1883 | 2.6737 | 4.0704 | 1693.859 | 677.5436 | 1016.3154 | 1219.3927 | 0.4 | 0.6 | 0.71989 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 542221.9607 | 813332.941 | 975850.8828 | 480127.7267 | 542221.9607 | 813332.941 | 975850.8828 | 1.05 | 1.3392 | 3.0131 | 4.3375 | 1693.8005 | 677.5202 | 1016.2803 | 1187.3385 | 0.4 | 0.6 | 0.70099 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 603522.6903 | 905284.0355 | 1057659.5426 | 506550.2462 | 603522.6903 | 905284.0355 | 1057659.5426 | 1.05 | 1.4905 | 3.3536 | 4.5776 | 1693.7419 | 677.4967 | 1016.2451 | 1157.5252 | 0.4 | 0.6 | 0.68341 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 665041.6681 | 997562.5022 | 1136245.3442 | 531750.2217 | 665041.6681 | 997562.5022 | 1136245.3442 | 1.05 | 1.6424 | 3.6953 | 4.7942 | 1693.683 | 677.4732 | 1016.2098 | 1129.679 | 0.4 | 0.6 | 0.667 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 726781.0396 | 1090171.5594 | 1211899.3275 | 555894.779 | 726781.0396 | 1090171.5594 | 1211899.3275 | 1.05 | 1.7948 | 4.0383 | 4.9904 | 1693.6239 | 677.4495 | 1016.1743 | 1103.5613 | 0.4 | 0.6 | 0.6516 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 788742.9861 | 1183114.4792 | 1284857.6398 | 579116.7594 | 788742.9861 | 1183114.4792 | 1284857.6398 | 1.05 | 1.9477 | 4.3824 | 5.1685 | 1693.5646 | 677.4258 | 1016.1387 | 1078.9587 | 0.4 | 0.6 | 0.63709 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 850929.7255 | 1276394.5883 | 1355304.1109 | 601523.8225 | 850929.7255 | 1276394.5883 | 1355304.1109 | 1.05 | 2.1012 | 4.7277 | 5.3304 | 1693.505 | 677.402 | 1016.103 | 1055.6726 | 0.4 | 0.6 | 0.62337 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 913343.5121 | 1370015.2681 | 1423367.1489 | 623204.6606 | 913343.5121 | 1370015.2681 | 1423367.1489 | 1.05 | 2.2553 | 5.0743 | 5.4772 | 1693.4452 | 677.3781 | 1016.0671 | 1033.5068 | 0.4 | 0.6 | 0.6103 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 975986.6372 | 1463979.9557 | 1489107.5699 | 644233.3713 | 975986.6372 | 1463979.9557 | 1489107.5699 | 1.05 | 2.4099 | 5.4222 | 5.6099 | 1693.3853 | 677.3541 | 1012.2472 | 1012.2472 | 0.4 | 0.59777 | 0.59777 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1038861.4293 | 1552488.683 | 1552488.683 | 664672.614 | 1038861.4293 | 1552488.683 | 1552488.683 | 1.05 | 2.565 | 5.7284 | 5.7284 | 1693.325 | 677.33 | 991.6235 | 991.6235 | 0.4 | 0.58561 | 0.58561 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1101970.2545 | 1613304.5116 | 1613304.5116 | 684575.9408 | 1101970.2545 | 1613304.5116 | 1613304.5116 | 1.05 | 2.7207 | 5.8315 | 5.8315 | 1693.2646 | 677.3058 | 971.2117 | 971.2117 | 0.4 | 0.57357 | 0.57357 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1165315.517 | 1670985.2942 | 1670985.2942 | 703989.5497 | 1165315.517 | 1670985.2942 | 1670985.2942 | 1.05 | 2.877 | 5.9156 | 5.9156 | 1693.2039 | 677.2816 | 950.0897 | 950.0897 | 0.4 | 0.56112 | 0.56112 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1228899.6588 | 1723898.9053 | 1723898.9053 | 722953.6275 | 1228899.6588 | 1723898.9053 | 1723898.9053 | 1.05 | 3.0339 | 5.9702 | 5.9702
850 | 1691.921 | 676.7684 | 1015.1526 | 1353.5368 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 236735.0221 | 355102.5331 | 473470.0441 | 317430.077 | 0.53635 | 355102.5331 | 473470.0441 | 1.05 | 1.05 | 1.314 | 2.336 | 1691.8641 | 676.7457 | 1015.1185 | 1353.4913 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 296409.2416 | 444613.8625 | 592818.4833 | 355197.5735 | 0.47933 | 444613.8625 | 592818.4833 | 1.05 | 1.05 | 1.6452 | 2.9248 | 1691.807 | 676.7228 | 1015.0842 | 1332.8033 | 0.4 | 0.6 | 0.7878 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 356283.1908 | 534424.7862 | 701698.5342 | 389429.7387 | 0.43721 | 534424.7862 | 701698.5342 | 1.05 | 1.05 | 1.9774 | 3.409 | 1691.7498 | 676.6999 | 1015.0499 | 1292.0383 | 0.4 | 0.6 | 0.76373 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 416358.6947 | 624538.042 | 794962.9789 | 420990.8121 | 0.40445 | 624538.042 | 794962.9789 | 1.05 | 1.05 | 2.3108 | 3.744 | 1691.6923 | 676.6769 | 1015.0154 | 1254.6492 | 0.4 | 0.6 | 0.74165 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 476637.6089 | 714956.4134 | 883749.6877 | 450443.5056 | 476637.6089 | 714956.4134 | 883749.6877 | 1.05 | 1.1757 | 2.6453 | 4.0417 | 1691.6346 | 676.6538 | 1014.9808 | 1220.1809 | 0.4 | 0.6 | 0.7213 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 537121.8203 | 805682.7305 | 968568.7657 | 478178.4252 | 537121.8203 | 805682.7305 | 968568.7657 | 1.05 | 1.3248 | 2.9808 | 4.3079 | 1691.5767 | 676.6307 | 1014.946 | 1188.256 | 0.4 | 0.6 | 0.70245 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 597813.2468 | 896719.8701 | 1049841.7833 | 504479.7942 | 597813.2468 | 896719.8701 | 1049841.7833 | 1.05 | 1.4745 | 3.3175 | 4.5473 | 1691.5187 | 676.6075 | 1014.9112 | 1158.5575 | 0.4 | 0.6 | 0.68492 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 658713.8376 | 988070.7564 | 1127918.2159 | 529562.0545 | 658713.8376 | 988070.7564 | 1127918.2159 | 1.05 | 1.6246 | 3.6554 | 4.7633 | 1691.4604 | 676.5841 | 1014.8762 | 1130.8149 | 0.4 | 0.6 | 0.66854 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 719825.5738 | 1079738.3607 | 1203086.8542 | 553591.7172 | 719825.5738 | 1079738.3607 | 1203086.8542 | 1.05 | 1.7753 | 3.9944 | 4.9591 | 1691.4019 | 676.5608 | 1014.8411 | 1104.7927 | 0.4 | 0.6 | 0.65318 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 781150.4683 | 1171725.7025 | 1275582.9603 | 576701.1345 | 781150.4683 | 1171725.7025 | 1275582.9603 | 1.05 | 1.9264 | 4.3345 | 5.1369 | 1691.3432 | 676.5373 | 1014.8059 | 1080.281 | 0.4 | 0.6 | 0.63871 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 842690.5663 | 1264035.8494 | 1345591.2035 | 598997.5687 | 842690.5663 | 1264035.8494 | 1345591.2035 | 1.05 | 2.0781 | 4.6758 | 5.2987 | 1691.2843 | 676.5137 | 1014.7706 | 1057.0852 | 0.4 | 0.6 | 0.62502 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 904447.9452 | 1356671.9178 | 1413243.3941 | 620569.384 | 904447.9452 | 1356671.9178 | 1413243.3941 | 1.05 | 2.2304 | 5.0183 | 5.4456 | 1691.2251 | 676.4901 | 1014.7351 | 1035.0146 | 0.4 | 0.6 | 0.61199 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 966424.7152 | 1449637.0728 | 1478608.1477 | 641490.4025 | 966424.7152 | 1449637.0728 | 1478608.1477 | 1.05 | 2.3831 | 5.362 | 5.5785 | 1691.1658 | 676.4663 | 1013.8647 | 1013.8647 | 0.4 | 0.59951 | 0.59951 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1028623.0195 | 1541665.2032 | 1541665.2032 | 661823.0494 | 1028623.0195 | 1541665.2032 | 1541665.2032 | 1.05 | 2.5364 | 5.6975 | 5.6975 | 1691.1062 | 676.4425 | 993.3837 | 993.3837 | 0.4 | 0.58742 | 0.58742 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1091045.0342 | 1602244.6744 | 1602244.6744 | 681620.675 | 1091045.0342 | 1602244.6744 | 1602244.6744 | 1.05 | 2.6902 | 5.8018 | 5.8018 | 1691.0465 | 676.4186 | 973.1926 | 973.1926 | 0.4 | 0.5755 | 0.5755 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1153692.9693 | 1659867.9329 | 1659867.9329 | 700929.3019 | 1153692.9693 | 1659867.9329 | 1659867.9329 | 1.05 | 2.8446 | 5.8883 | 5.8883 | 1690.9864 | 676.3946 | 952.5223 | 952.5223 | 0.4 | 0.56329 | 0.56329 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1216569.0681 | 1713214.6635 | 1713214.6635 | 719788.9627 | 1216569.0681 | 1713214.6635 | 1713214.6635 | 1.05 | 2.9995 | 5.9484 | 5.9484
860 | 1689.6909 | 675.8764 | 1013.8145 | 1351.7527 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 234585.1564 | 351877.7346 | 469170.3128 | 316193.9049 | 0.53915 | 351877.7346 | 469170.3128 | 1.05 | 1.05 | 1.3004 | 2.3118 | 1689.6345 | 675.8538 | 1013.7807 | 1351.7076 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 293702.7145 | 440554.0717 | 587405.429 | 353805.3965 | 0.48186 | 440554.0717 | 587405.429 | 1.05 | 1.05 | 1.628 | 2.8943 | 1689.578 | 675.8312 | 1013.7468 | 1333.0406 | 0.4 | 0.6 | 0.78898 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 353012.0698 | 529518.1047 | 696297.2709 | 387893.5132 | 0.43952 | 529518.1047 | 696297.2709 | 1.05 | 1.05 | 1.9567 | 3.3834 | 1689.5213 | 675.8085 | 1013.7128 | 1292.474 | 0.4 | 0.6 | 0.76499 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 412514.9144 | 618772.3716 | 788928.8045 | 419319.3062 | 0.4066 | 618772.3716 | 788928.8045 | 1.05 | 1.05 | 2.2864 | 3.7169 | 1689.4643 | 675.7857 | 1013.6786 | 1255.2546 | 0.4 | 0.6 | 0.74299 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 472212.9678 | 708319.4517 | 877123.4026 | 448643.4191 | 472212.9678 | 708319.4517 | 877123.4026 | 1.05 | 1.1632 | 2.6172 | 4.0134 | 1689.4072 | 675.7629 | 1013.6443 | 1220.9329 | 0.4 | 0.6 | 0.7227 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 532107.9768 | 798161.9653 | 961384.7364 | 476255.0269 | 532107.9768 | 798161.9653 | 961384.7364 | 1.05 | 1.3107 | 2.9491 | 4.2786 | 1689.3499 | 675.74 | 1013.6099 | 1189.1363 | 0.4 | 0.6 | 0.7039 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 592201.7162 | 888302.5744 | 1042129.5337 | 502437.3136 | 592201.7162 | 888302.5744 | 1042129.5337 | 1.05 | 1.4587 | 3.2821 | 4.5172 | 1689.2924 | 675.717 | 1013.5754 | 1159.5517 | 0.4 | 0.6 | 0.68641 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 652495.9886 | 978743.9829 | 1119703.755 | 527403.9383 | 652495.9886 | 978743.9829 | 1119703.755 | 1.05 | 1.6072 | 3.6161 | 4.7327 | 1689.2347 | 675.6939 | 1013.5408 | 1131.9116 | 0.4 | 0.6 | 0.67007 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 712992.6245 | 1069488.9368 | 1194393.8989 | 551320.8043 | 712992.6245 | 1069488.9368 | 1194393.8989 | 1.05 | 1.7561 | 3.9512 | 4.9281 | 1689.1768 | 675.6707 | 1013.5061 | 1105.9839 | 0.4 | 0.6 | 0.65475 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 773693.4831 | 1160540.2247 | 1266434.2259 | 574319.7808 | 773693.4831 | 1160540.2247 | 1266434.2259 | 1.05 | 1.9055 | 4.2875 | 5.1056 | 1689.1187 | 675.6475 | 1013.4712 | 1081.5616 | 0.4 | 0.6 | 0.64031 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 834600.4519 | 1251900.6778 | 1336010.0039 | 596507.7379 | 834600.4519 | 1251900.6778 | 1336010.0039 | 1.05 | 2.0555 | 4.6248 | 5.2672 | 1689.0604 | 675.6242 | 1013.4363 | 1058.4541 | 0.4 | 0.6 | 0.62665 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 895715.447 | 1343573.1704 | 1403255.9697 | 617972.7158 | 895715.447 | 1343573.1704 | 1403255.9697 | 1.05 | 2.2059 | 4.9633 | 5.4141 | 1689.0019 | 675.6008 | 1013.4011 | 1036.4758 | 0.4 | 0.6 | 0.61366 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 957040.4136 | 1435560.6203 | 1468247.5787 | 638788.2651 | 957040.4136 | 1435560.6203 | 1468247.5787 | 1.05 | 2.3569 | 5.303 | 5.5472 | 1688.9432 | 675.5773 | 1013.3659 | 1015.4306 | 0.4 | 0.6 | 0.60122 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1018577.3259 | 1527865.9888 | 1530978.9144 | 659016.5802 | 1018577.3259 | 1527865.9888 | 1530978.9144 | 1.05 | 2.5083 | 5.6437 | 5.6668 | 1688.8843 | 675.5537 | 995.0829 | 995.0829 | 0.4 | 0.5892 | 0.5892 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1080328.1875 | 1591311.0346 | 1591311.0346 | 678710.813 | 1080328.1875 | 1591311.0346 | 1591311.0346 | 1.05 | 2.6603 | 5.772 | 5.772 | 1688.8252 | 675.5301 | 975.0909 | 975.0909 | 0.4 | 0.57738 | 0.57738 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1142295.0316 | 1648840.6943 | 1648840.6943 | 697916.8136 | 1142295.0316 | 1648840.6943 | 1648840.6943 | 1.05 | 2.8128 | 5.8606 | 5.8606 | 1688.7658 | 675.5063 | 954.8024 | 954.8024 | 0.4 | 0.56538 | 0.56538 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1204479.9208 | 1702486.4454 | 1702486.4454 | 716674.463 | 1204479.9208 | 1702486.4454 | 1702486.4454 | 1.05 | 2.9658 | 5.9253 | 5.9253
870 | 1687.4578 | 674.9831 | 1012.4747 | 1349.9662 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 232468.967 | 348703.4505 | 464937.9341 | 314972.6876 | 0.54196 | 348703.4505 | 464937.9341 | 1.05 | 1.05 | 1.2869 | 2.2879 | 1687.4019 | 674.9608 | 1012.4412 | 1349.9216 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 291039.1488 | 436558.7232 | 582078.2976 | 352430.3443 | 0.48438 | 436558.7232 | 582078.2976 | 1.05 | 1.05 | 1.6111 | 2.8642 | 1687.3459 | 674.9384 | 1012.4076 | 1333.2464 | 0.4 | 0.6 | 0.79014 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 349793.5622 | 524690.3433 | 690968.2573 | 386376.499 | 0.44183 | 524690.3433 | 690968.2573 | 1.05 | 1.05 | 1.9363 | 3.358 | 1687.2897 | 674.9159 | 1012.3738 | 1292.8766 | 0.4 | 0.6 | 0.76624 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 408733.7772 | 613100.6657 | 782975.0806 | 417669.0487 | 0.40874 | 613100.6657 | 782975.0806 | 1.05 | 1.05 | 2.2625 | 3.69 | 1687.2334 | 674.8933 | 1012.34 | 1255.8255 | 0.4 | 0.6 | 0.74431 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 467861.3879 | 701792.0819 | 870585.3565 | 446866.5912 | 467861.3879 | 701792.0819 | 870585.3565 | 1.05 | 1.151 | 2.5897 | 3.9853 | 1687.1768 | 674.8707 | 1012.3061 | 1221.6494 | 0.4 | 0.6 | 0.72408 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 527178.0132 | 790767.0198 | 954296.4121 | 474356.8853 | 527178.0132 | 790767.0198 | 954296.4121 | 1.05 | 1.2969 | 2.9179 | 4.2496 | 1687.1201 | 674.848 | 1012.272 | 1189.9802 | 0.4 | 0.6 | 0.70533 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 586685.2964 | 880027.9446 | 1034520.1825 | 500422.0872 | 586685.2964 | 880027.9446 | 1034520.1825 | 1.05 | 1.4432 | 3.2472 | 4.4874 | 1687.0631 | 674.8252 | 1012.2379 | 1160.5085 | 0.4 | 0.6 | 0.68789 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 646384.9057 | 969577.3586 | 1111599.1244 | 525275.082 | 646384.9057 | 969577.3586 | 1111599.1244 | 1.05 | 1.59 | 3.5775 | 4.7023 | 1687.006 | 674.8024 | 1012.2036 | 1132.9701 | 0.4 | 0.6 | 0.67159 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 706278.5343 | 1059417.8014 | 1185817.4087 | 549081.1724 | 706278.5343 | 1059417.8014 | 1185817.4087 | 1.05 | 1.7373 | 3.9089 | 4.8972 | 1686.9487 | 674.7795 | 1012.1692 | 1107.1357 | 0.4 | 0.6 | 0.65629 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 766367.9003 | 1149551.8504 | 1257408.1917 | 571971.7498 | 766367.9003 | 1149551.8504 | 1257408.1917 | 1.05 | 1.885 | 4.2413 | 5.0745 | 1686.8912 | 674.7565 | 1012.1347 | 1082.8015 | 0.4 | 0.6 | 0.64189 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 826654.7473 | 1239982.1209 | 1326557.1253 | 594053.2973 | 826654.7473 | 1239982.1209 | 1326557.1253 | 1.05 | 2.0332 | 4.5748 | 5.2359 | 1686.8335 | 674.7334 | 1012.1001 | 1059.7804 | 0.4 | 0.6 | 0.62827 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 887140.8442 | 1330711.2662 | 1393401.4531 | 615413.5352 | 887140.8442 | 1330711.2662 | 1393401.4531 | 1.05 | 2.1819 | 4.9093 | 5.3828 | 1686.7756 | 674.7102 | 1012.0653 | 1037.8917 | 0.4 | 0.6 | 0.61531 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 947827.9855 | 1421741.9782 | 1458022.6325 | 636125.7461 | 947827.9855 | 1421741.9782 | 1458022.6325 | 1.05 | 2.3311 | 5.245 | 5.5161 | 1686.7175 | 674.687 | 1012.0305 | 1016.9468 | 0.4 | 0.6 | 0.60291 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1008717.9916 | 1513076.9874 | 1520427.3048 | 656251.897 | 1008717.9916 | 1513076.9874 | 1520427.3048 | 1.05 | 2.4808 | 5.5817 | 5.6361 | 1686.6592 | 674.6637 | 996.7241 | 996.7241 | 0.4 | 0.59095 | 0.59095 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1069812.7086 | 1580503.1911 | 1580503.1911 | 675844.9444 | 1069812.7086 | 1580503.1911 | 1580503.1911 | 1.05 | 2.6309 | 5.7423 | 5.7423 | 1686.6007 | 674.6403 | 976.913 | 976.913 | 0.4 | 0.57922 | 0.57922 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1131114.0088 | 1637909.9616 | 1637909.9616 | 694950.5686 | 1131114.0088 | 1637909.9616 | 1637909.9616 | 1.05 | 2.7816 | 5.8326 | 5.8326 | 1686.542 | 674.6168 | 956.953 | 956.953 | 0.4 | 0.56741 | 0.56741 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1192623.7908 | 1691752.8874 | 1691752.8874 | 713608.5019 | 1192623.7908 | 1691752.8874 | 1691752.8874 | 1.05 | 2.9328 | 5.9012 | 5.9012
880 | 1685.2217 | 674.0887 | 1011.133 | 1348.1773 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 230385.6211 | 345578.4317 | 460771.2423 | 313766.1061 | 0.54477 | 345578.4317 | 460771.2423 | 1.05 | 1.05 | 1.2737 | 2.2644 | 1685.1664 | 674.0665 | 1011.0998 | 1348.1331 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 288417.4574 | 432626.1861 | 576834.9149 | 351072.0404 | 0.48689 | 432626.1861 | 576834.9149 | 1.05 | 1.05 | 1.5945 | 2.8347 | 1685.1109 | 674.0443 | 1011.0665 | 1333.4212 | 0.4 | 0.6 | 0.7913 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 346626.3062 | 519939.4593 | 685709.8529 | 384878.2613 | 0.44414 | 519939.4593 | 685709.8529 | 1.05 | 1.05 | 1.9162 | 3.3329 | 1685.0552 | 674.0221 | 1011.0331 | 1293.2467 | 0.4 | 0.6 | 0.76748 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 405013.6251 | 607520.4377 | 777099.9494 | 416039.5451 | 0.41089 | 607520.4377 | 777099.9494 | 1.05 | 1.05 | 2.2389 | 3.6633 | 1684.9994 | 673.9997 | 1010.9996 | 1256.3627 | 0.4 | 0.6 | 0.74562 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 463580.8933 | 695371.34 | 864133.4752 | 445112.465 | 463580.8933 | 695371.34 | 864133.4752 | 1.05 | 1.1389 | 2.5626 | 3.9574 | 1684.9433 | 673.9773 | 1010.966 | 1222.3311 | 0.4 | 0.6 | 0.72544 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 522329.6119 | 783494.4178 | 947301.5014 | 472483.3792 | 522329.6119 | 783494.4178 | 947301.5014 | 1.05 | 1.2832 | 2.8873 | 4.2208 | 1684.8871 | 673.9549 | 1010.9323 | 1190.7884 | 0.4 | 0.6 | 0.70675 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 581261.3037 | 871891.9555 | 1027011.2212 | 498433.4272 | 581261.3037 | 871891.9555 | 1027011.2212 | 1.05 | 1.428 | 3.2129 | 4.4578 | 1684.8308 | 673.9323 | 1010.8985 | 1161.4286 | 0.4 | 0.6 | 0.68934 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 640377.5137 | 960566.2705 | 1103601.6015 | 523174.7284 | 640377.5137 | 960566.2705 | 1103601.6015 | 1.05 | 1.5731 | 3.5396 | 4.6722 | 1684.7742 | 673.9097 | 1010.8645 | 1133.9909 | 0.4 | 0.6 | 0.67308 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 699679.809 | 1049519.7135 | 1177354.4562 | 546871.9914 | 699679.809 | 1049519.7135 | 1177354.4562 | 1.05 | 1.7188 | 3.8672 | 4.8667 | 1684.7175 | 673.887 | 1010.8305 | 1108.2489 | 0.4 | 0.6 | 0.65782 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 759169.779 | 1138754.6685 | 1248501.7468 | 569656.1358 | 759169.779 | 1138754.6685 | 1248501.7468 | 1.05 | 1.8648 | 4.1959 | 5.0436 | 1684.6605 | 673.8642 | 1010.7963 | 1084.0016 | 0.4 | 0.6 | 0.64345 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 818849.0355 | 1228273.5532 | 1317229.3182 | 591633.2619 | 818849.0355 | 1228273.5532 | 1317229.3182 | 1.05 | 2.0114 | 4.5256 | 5.2048 | 1684.6034 | 673.8414 | 1010.762 | 1061.0653 | 0.4 | 0.6 | 0.62986 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 878719.2127 | 1318078.8191 | 1383676.5492 | 612890.7744 | 878719.2127 | 1318078.8191 | 1383676.5492 | 1.05 | 2.1584 | 4.8563 | 5.3517 | 1684.5461 | 673.8184 | 1010.7277 | 1039.2637 | 0.4 | 0.6 | 0.61694 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 938781.9677 | 1408172.9515 | 1447930.1653 | 633501.6914 | 938781.9677 | 1408172.9515 | 1447930.1653 | 1.05 | 2.3058 | 5.1881 | 5.4852 | 1684.4886 | 673.7954 | 1010.6932 | 1018.4151 | 0.4 | 0.6 | 0.60458 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 999038.9801 | 1498558.4701 | 1510007.8282 | 653527.7555 | 999038.9801 | 1498558.4701 | 1510007.8282 | 1.05 | 2.4537 | 5.5209 | 5.6056 | 1684.4309 | 673.7724 | 998.3102 | 998.3102 | 0.4 | 0.59267 | 0.59267 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1059491.9526 | 1569820.337 | 1569820.337 | 673021.7305 | 1059491.9526 | 1569820.337 | 1569820.337 | 1.05 | 2.6021 | 5.7126 | 5.7126 | 1684.3731 | 673.7492 | 978.6648 | 978.6648 | 0.4 | 0.58103 | 0.58103 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1120142.611 | 1627080.2887 | 1627080.2887 | 692029.1297 | 1120142.611 | 1627080.2887 | 1627080.2887 | 1.05 | 2.751 | 5.8044 | 5.8044 | 1684.315 | 673.726 | 958.9909 | 958.9909 | 0.4 | 0.56937 | 0.56937 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1180992.7041 | 1681041.3862 | 1681041.3862 | 710589.5393 | 1180992.7041 | 1681041.3862 | 1681041.3862 | 1.05 | 2.9003 | 5.8764 | 5.8764
890 | 1682.9826 | 673.193 | 1009.7895 | 1346.3861 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 228334.3147 | 342501.472 | 456668.6294 | 312573.8517 | 0.54757 | 342501.472 | 456668.6294 | 1.05 | 1.05 | 1.2607 | 2.2412 | 1682.9277 | 673.1711 | 1009.7566 | 1346.3422 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 285836.5921 | 428754.8881 | 571673.1842 | 349730.121 | 0.48941 | 428754.8881 | 571673.1842 | 1.05 | 1.05 | 1.5781 | 2.8056 | 1682.8728 | 673.1491 | 1009.7237 | 1333.5655 | 0.4 | 0.6 | 0.79243 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 343508.9904 | 515263.4856 | 680520.4732 | 383398.3805 | 0.44645 | 515263.4856 | 680520.4732 | 1.05 | 1.05 | 1.8965 | 3.308 | 1682.8176 | 673.127 | 1009.6906 | 1293.5848 | 0.4 | 0.6 | 0.7687 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 401352.8638 | 602029.2957 | 771301.619 | 414430.3183 | 0.41303 | 602029.2957 | 771301.619 | 1.05 | 1.05 | 2.2158 | 3.6369 | 1682.7623 | 673.1049 | 1009.6574 | 1256.8667 | 0.4 | 0.6 | 0.74691 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 459369.5858 | 689054.3787 | 857765.7601 | 443380.5048 | 459369.5858 | 689054.3787 | 857765.7601 | 1.05 | 1.1271 | 2.536 | 3.9298 | 1682.7068 | 673.0827 | 1009.6241 | 1222.9787 | 0.4 | 0.6 | 0.72679 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 517560.5492 | 776340.8237 | 940397.799 | 470633.912 | 517560.5492 | 776340.8237 | 940397.799 | 1.05 | 1.2698 | 2.8571 | 4.1922 | 1682.6512 | 673.0605 | 1009.5907 | 1191.5614 | 0.4 | 0.6 | 0.70815 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 575927.1662 | 863890.7492 | 1019600.2384 | 496470.6736 | 575927.1662 | 863890.7492 | 1019600.2384 | 1.05 | 1.413 | 3.1792 | 4.4286 | 1682.5953 | 673.0381 | 1009.5572 | 1162.3129 | 0.4 | 0.6 | 0.69079 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 634470.8687 | 951706.303 | 1095708.5718 | 521102.1514 | 634470.8687 | 951706.303 | 1095708.5718 | 1.05 | 1.5566 | 3.5023 | 4.6423 | 1682.5393 | 673.0157 | 1009.5236 | 1134.9751 | 0.4 | 0.6 | 0.67456 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 693193.1082 | 1039789.6623 | 1169002.2322 | 544692.4669 | 693193.1082 | 1039789.6623 | 1169002.2322 | 1.05 | 1.7006 | 3.8263 | 4.8363 | 1682.4831 | 672.9933 | 1009.4899 | 1109.3244 | 0.4 | 0.6 | 0.65934 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 752095.356 | 1128143.034 | 1239711.9061 | 567372.0729 | 752095.356 | 1128143.034 | 1239711.9061 | 1.05 | 1.845 | 4.1513 | 5.013 | 1682.4268 | 672.9707 | 1009.4561 | 1085.1629 | 0.4 | 0.6 | 0.645 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 811179.1032 | 1216768.6549 | 1308023.4623 | 589246.6915 | 811179.1032 | 1216768.6549 | 1308023.4623 | 1.05 | 1.9899 | 4.4772 | 5.174 | 1682.3702 | 672.9481 | 1009.4221 | 1062.3099 | 0.4 | 0.6 | 0.63144 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 870445.861 | 1305668.7915 | 1374078.0843 | 610403.4154 | 870445.861 | 1305668.7915 | 1374078.0843 | 1.05 | 2.1352 | 4.8042 | 5.3208 | 1682.3135 | 672.9254 | 1009.3881 | 1040.5931 | 0.4 | 0.6 | 0.61855 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 929897.1605 | 1394845.7407 | 1437967.1213 | 630915.0018 | 929897.1605 | 1394845.7407 | 1437967.1213 | 1.05 | 2.281 | 5.1322 | 5.4544 | 1682.2566 | 672.9027 | 1009.354 | 1019.8372 | 0.4 | 0.6 | 0.60623 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 989534.5529 | 1484301.8294 | 1499717.9266 | 650842.9718 | 989534.5529 | 1484301.8294 | 1499717.9266 | 1.05 | 2.4272 | 5.4611 | 5.5751 | 1682.1995 | 672.8798 | 999.8436 | 999.8436 | 0.4 | 0.59437 | 0.59437 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1049359.6099 | 1559261.355 | 1559261.355 | 670239.8993 | 1049359.6099 | 1559261.355 | 1559261.355 | 1.05 | 2.5738 | 5.6829 | 5.6829 | 1682.1423 | 672.8569 | 980.3507 | 980.3507 | 0.4 | 0.5828 | 0.5828 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1109373.9234 | 1616354.8449 | 1616354.8449 | 689151.1331 | 1109373.9234 | 1616354.8449 | 1616354.8449 | 1.05 | 2.7209 | 5.7761 | 5.7761 | 1682.0848 | 672.8339 | 960.9293 | 960.9293 | 0.4 | 0.57127 | 0.57127 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1169579.1058 | 1670371.7896 | 1670371.7896 | 707616.1152 | 1169579.1058 | 1670371.7896 | 1670371.7896 | 1.05 | 2.8685 | 5.8509 | 5.8509
900 | 1680.7404 | 672.2962 | 1008.4443 | 1344.5924 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 226314.2712 | 339471.4068 | 452628.5424 | 311395.6255 | 0.55038 | 339471.4068 | 452628.5424 | 1.05 | 1.05 | 1.2479 | 2.2184 | 1680.6861 | 672.2744 | 1008.4117 | 1344.5489 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 283295.5416 | 424943.3124 | 566591.0831 | 348404.2345 | 0.49193 | 424943.3124 | 566591.0831 | 1.05 | 1.05 | 1.562 | 2.7769 | 1680.6316 | 672.2527 | 1008.379 | 1333.68 | 0.4 | 0.6 | 0.79356 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 340440.3512 | 510660.5268 | 675398.5868 | 381936.4514 | 0.44876 | 510660.5268 | 675398.5868 | 1.05 | 1.05 | 1.877 | 3.2834 | 1680.577 | 672.2308 | 1008.3462 | 1293.8917 | 0.4 | 0.6 | 0.76991 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 397749.9589 | 596624.9383 | 765578.3596 | 412840.9089 | 0.41518 | 596624.9383 | 765578.3596 | 1.05 | 1.05 | 2.1929 | 3.6108 | 1680.5222 | 672.2089 | 1008.3133 | 1257.3382 | 0.4 | 0.6 | 0.74818 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 455225.6408 | 682838.4612 | 851480.2841 | 441670.1948 | 455225.6408 | 682838.4612 | 851480.2841 | 1.05 | 1.1154 | 2.5097 | 3.9025 | 1680.4672 | 672.1869 | 1008.2803 | 1223.5927 | 0.4 | 0.6 | 0.72813 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 512868.6901 | 769303.0351 | 933583.181 | 468807.9099 | 512868.6901 | 769303.0351 | 933583.181 | 1.05 | 1.2566 | 2.8274 | 4.1639 | 1680.4121 | 672.1648 | 1008.2473 | 1192.3001 | 0.4 | 0.6 | 0.70953 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 570680.4174 | 856020.6261 | 1012284.9141 | 494533.1925 | 570680.4174 | 856020.6261 | 1012284.9141 | 1.05 | 1.3982 | 3.1461 | 4.3995 | 1680.3568 | 672.1427 | 1008.2141 | 1163.1619 | 0.4 | 0.6 | 0.69221 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 628662.1506 | 942993.2259 | 1087917.5221 | 519056.655 | 628662.1506 | 942993.2259 | 1087917.5221 | 1.05 | 1.5403 | 3.4656 | 4.6127 | 1680.3013 | 672.1205 | 1008.1808 | 1135.9231 | 0.4 | 0.6 | 0.67602 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 686815.2352 | 1030222.8528 | 1160758.0381 | 542541.8378 | 686815.2352 | 1030222.8528 | 1160758.0381 | 1.05 | 1.6827 | 3.786 | 4.8062 | 1680.2457 | 672.0983 | 1008.1474 | 1110.363 | 0.4 | 0.6 | 0.66083 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 745141.0341 | 1117711.5512 | 1231035.8034 | 565118.7325 | 745141.0341 | 1117711.5512 | 1231035.8034 | 1.05 | 1.8255 | 4.1074 | 4.9825 | 1680.1899 | 672.076 | 1008.1139 | 1086.2862 | 0.4 | 0.6 | 0.64653 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 803640.9278 | 1205461.3917 | 1298936.5593 | 586892.6872 | 803640.9278 | 1205461.3917 | 1298936.5593 | 1.05 | 1.9688 | 4.4297 | 5.1434 | 1680.1339 | 672.0536 | 1008.0804 | 1063.515 | 0.4 | 0.6 | 0.63299 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 862316.3146 | 1293474.4719 | 1364603.0009 | 607950.4864 | 862316.3146 | 1293474.4719 | 1364603.0009 | 1.05 | 2.1124 | 4.753 | 5.2901 | 1680.0778 | 672.0311 | 1008.0467 | 1041.8811 | 0.4 | 0.6 | 0.62014 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 921168.6104 | 1381752.9156 | 1428130.5327 | 628364.6293 | 921168.6104 | 1381752.9156 | 1428130.5327 | 1.05 | 2.2565 | 5.0772 | 5.4238 | 1680.0215 | 672.0086 | 1008.0129 | 1021.2146 | 0.4 | 0.6 | 0.60786 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 980199.249 | 1470298.8735 | 1489555.0471 | 648196.4186 | 980199.249 | 1470298.8735 | 1489555.0471 | 1.05 | 2.4011 | 5.4024 | 5.5448 | 1679.965 | 671.986 | 1001.3267 | 1001.3267 | 0.4 | 0.59604 | 0.59604 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1039409.6822 | 1548824.8923 | 1548824.8923 | 667498.2409 | 1039409.6822 | 1548824.8923 | 1548824.8923 | 1.05 | 2.546 | 5.6532 | 5.6532 | 1679.9083 | 671.9633 | 981.975 | 981.975 | 0.4 | 0.58454 | 0.58454 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1098801.3796 | 1605735.7397 | 1605735.7397 | 686315.2825 | 1098801.3796 | 1605735.7397 | 1605735.7397 | 1.05 | 2.6914 | 5.7476 | 5.7476 | 1679.8515 | 671.9406 | 962.7784 | 962.7784 | 0.4 | 0.57313 | 0.57313 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1158375.8291 | 1659758.6903 | 1659758.6903 | 704686.8439 | 1158375.8291 | 1659758.6903 | 1659758.6903 | 1.05 | 2.8372 | 5.8249 | 5.8249
910 | 1678.1741 | 671.2696 | 1006.9044 | 1342.5393 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 224281.8115 | 336422.7172 | 448563.6229 | 310231.138 | 0.55329 | 336422.7172 | 448563.6229 | 1.05 | 1.05 | 1.2348 | 2.1952 | 1678.1202 | 671.2481 | 1006.8721 | 1342.4962 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 280739.5948 | 421109.3922 | 561479.1896 | 347094.0405 | 0.49454 | 421109.3922 | 561479.1896 | 1.05 | 1.05 | 1.5456 | 2.7477 | 1678.0663 | 671.2265 | 1006.8398 | 1333.5099 | 0.4 | 0.6 | 0.79467 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 337354.5988 | 506031.8982 | 670214.4303 | 380492.0827 | 0.45115 | 506031.8982 | 670214.4303 | 1.05 | 1.05 | 1.8572 | 3.2578 | 1678.0121 | 671.2049 | 1006.8073 | 1293.92 | 0.4 | 0.6 | 0.7711 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 394127.9944 | 591191.9915 | 759783.0738 | 411270.8731 | 0.4174 | 591191.9915 | 759783.0738 | 1.05 | 1.05 | 2.1697 | 3.5835 | 1677.9579 | 671.1831 | 1006.7747 | 1257.5371 | 0.4 | 0.6 | 0.74944 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 451060.9675 | 676591.4512 | 845113.4287 | 439981.038 | 451060.9675 | 676591.4512 | 845113.4287 | 1.05 | 1.1035 | 2.483 | 3.8739 | 1677.9034 | 671.1614 | 1006.7421 | 1223.9395 | 0.4 | 0.6 | 0.72945 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 508154.7195 | 762232.0793 | 926678.2291 | 467004.8207 | 508154.7195 | 762232.0793 | 926678.2291 | 1.05 | 1.2432 | 2.7972 | 4.1343 | 1677.8488 | 671.1395 | 1006.7093 | 1192.7767 | 0.4 | 0.6 | 0.7109 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 565410.4672 | 848115.7009 | 1004870.6767 | 492620.3745 | 565410.4672 | 848115.7009 | 1004870.6767 | 1.05 | 1.3832 | 3.1123 | 4.369 | 1677.7941 | 671.1176 | 1006.6764 | 1163.7536 | 0.4 | 0.6 | 0.69362 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 622829.4428 | 934244.1642 | 1080019.3131 | 517037.5706 | 622829.4428 | 934244.1642 | 1080019.3131 | 1.05 | 1.5236 | 3.4282 | 4.5815 | 1677.7391 | 671.0957 | 1006.6435 | 1136.6183 | 0.4 | 0.6 | 0.67747 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 680412.8939 | 1020619.3409 | 1152398.7042 | 540419.3744 | 680412.8939 | 1020619.3409 | 1152398.7042 | 1.05 | 1.6645 | 3.745 | 4.7746 | 1677.6841 | 671.0736 | 1006.6104 | 1111.1528 | 0.4 | 0.6 | 0.66231 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 738162.0837 | 1107243.1256 | 1222236.7409 | 562895.3212 | 738162.0837 | 1107243.1256 | 1222236.7409 | 1.05 | 1.8057 | 4.0627 | 4.9505 | 1677.6288 | 671.0515 | 1006.5773 | 1087.1642 | 0.4 | 0.6 | 0.64804 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 796078.291 | 1194117.4365 | 1289718.8666 | 584570.3893 | 796078.291 | 1194117.4365 | 1289718.8666 | 1.05 | 1.9473 | 4.3814 | 5.111 | 1677.5734 | 671.0294 | 1006.544 | 1064.4779 | 0.4 | 0.6 | 0.63453 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 854162.8103 | 1281244.2154 | 1354988.999 | 605531.0586 | 854162.8103 | 1281244.2154 | 1354988.999 | 1.05 | 2.0893 | 4.7009 | 5.2576 | 1677.5178 | 671.0071 | 1006.5107 | 1042.929 | 0.4 | 0.6 | 0.62171 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 912416.9517 | 1368625.4276 | 1418146.0776 | 625849.5736 | 912416.9517 | 1368625.4276 | 1418146.0776 | 1.05 | 2.2317 | 5.0213 | 5.3913 | 1677.4621 | 670.9848 | 1006.4773 | 1022.353 | 0.4 | 0.6 | 0.60946 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 970842.0412 | 1456263.0618 | 1479233.5212 | 645587.0211 | 970842.0412 | 1456263.0618 | 1479233.5212 | 1.05 | 2.3745 | 5.3427 | 5.5126 | 1677.4062 | 670.9625 | 1002.5695 | 1002.5695 | 0.4 | 0.59769 | 0.59769 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1029439.4205 | 1538214.9946 | 1538214.9946 | 664795.6028 | 1029439.4205 | 1538214.9946 | 1538214.9946 | 1.05 | 2.5178 | 5.6214 | 5.6214 | 1677.3501 | 670.94 | 983.353 | 983.353 | 0.4 | 0.58625 | 0.58625 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1088210.4473 | 1594918.988 | 1594918.988 | 683520.3451 | 1088210.4473 | 1594918.988 | 1594918.988 | 1.05 | 2.6614 | 5.7169 | 5.7169 | 1677.2939 | 670.9175 | 964.362 | 964.362 | 0.4 | 0.57495 | 0.57495 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1147156.4952 | 1648897.3079 | 1648897.3079 | 701800.4083 | 1147156.4952 | 1648897.3079 | 1648897.3079 | 1.05 | 2.8055 | 5.7963 | 5.7963
920 | 1675.6037 | 670.2415 | 1005.3622 | 1340.483 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 222279.6524 | 333419.4786 | 444559.3048 | 309080.1086 | 0.5562 | 333419.4786 | 444559.3048 | 1.05 | 1.05 | 1.2219 | 2.1722 | 1675.5504 | 670.2202 | 1005.3302 | 1340.4403 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 278222.1914 | 417333.2871 | 556444.3828 | 345799.2098 | 0.49716 | 417333.2871 | 556444.3828 | 1.05 | 1.05 | 1.5294 | 2.7188 | 1675.4969 | 670.1988 | 1005.2982 | 1333.3094 | 0.4 | 0.6 | 0.79577 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 334315.9126 | 501473.8688 | 665096.0561 | 379064.8961 | 0.45354 | 501473.8688 | 665096.0561 | 1.05 | 1.05 | 1.8376 | 3.2324 | 1675.4433 | 670.1773 | 1005.266 | 1293.9166 | 0.4 | 0.6 | 0.77228 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 390561.9053 | 585842.858 | 754060.9055 | 409719.783 | 0.41962 | 585842.858 | 754060.9055 | 1.05 | 1.05 | 2.1467 | 3.5565 | 1675.3895 | 670.1558 | 1005.2337 | 1257.703 | 0.4 | 0.6 | 0.75069 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 446961.2728 | 670441.9092 | 838826.61 | 438312.5552 | 446961.2728 | 670441.9092 | 838826.61 | 1.05 | 1.0918 | 2.4567 | 3.8456 | 1675.3356 | 670.1342 | 1005.2014 | 1224.2524 | 0.4 | 0.6 | 0.73075 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 503515.1317 | 755272.6976 | 919859.9035 | 465224.1126 | 503515.1317 | 755272.6976 | 919859.9035 | 1.05 | 1.23 | 2.7674 | 4.105 | 1675.2815 | 670.1126 | 1005.1689 | 1193.2186 | 0.4 | 0.6 | 0.71225 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 560224.6123 | 840336.9185 | 997549.379 | 490731.6338 | 560224.6123 | 840336.9185 | 997549.379 | 1.05 | 1.3684 | 3.079 | 4.3388 | 1675.2273 | 670.0909 | 1005.1364 | 1164.3098 | 0.4 | 0.6 | 0.69502 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 617090.8586 | 925636.288 | 1072220.1042 | 515044.2562 | 617090.8586 | 925636.288 | 1072220.1042 | 1.05 | 1.5073 | 3.3914 | 4.5506 | 1675.1729 | 670.0692 | 1005.1037 | 1137.2773 | 0.4 | 0.6 | 0.6789 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 674115.0285 | 1011172.5427 | 1144144.1681 | 538324.3765 | 674115.0285 | 1011172.5427 | 1144144.1681 | 1.05 | 1.6465 | 3.7047 | 4.7431 | 1675.1184 | 670.0473 | 1005.071 | 1111.9055 | 0.4 | 0.6 | 0.66378 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 731298.2934 | 1096947.44 | 1213547.9569 | 560701.0784 | 731298.2934 | 1096947.44 | 1213547.9569 | 1.05 | 1.7861 | 4.0188 | 4.9186 | 1675.0637 | 670.0255 | 1005.0382 | 1088.0042 | 0.4 | 0.6 | 0.64953 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 788641.8386 | 1182962.758 | 1280616.496 | 582278.9747 | 788641.8386 | 1182962.758 | 1280616.496 | 1.05 | 1.9261 | 4.3338 | 5.0788 | 1675.0088 | 670.0035 | 1005.0053 | 1065.4016 | 0.4 | 0.6 | 0.63606 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 846146.8635 | 1269220.2953 | 1345494.6922 | 603144.2441 | 846146.8635 | 1269220.2953 | 1345494.6922 | 1.05 | 2.0665 | 4.6497 | 5.2253 | 1674.9538 | 669.9815 | 1004.9723 | 1043.9361 | 0.4 | 0.6 | 0.62326 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 903814.5811 | 1355721.8717 | 1408284.5742 | 623368.8791 | 903814.5811 | 1355721.8717 | 1408284.5742 | 1.05 | 2.2073 | 4.9664 | 5.359 | 1674.8986 | 669.9595 | 1004.9392 | 1023.4478 | 0.4 | 0.6 | 0.61105 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 961646.2185 | 1442469.3278 | 1469036.2074 | 643013.7536 | 961646.2185 | 1442469.3278 | 1469036.2074 | 1.05 | 2.3484 | 5.284 | 5.4804 | 1674.8433 | 669.9373 | 1003.7642 | 1003.7642 | 0.4 | 0.59932 | 0.59932 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1019643.0167 | 1527726.6965 | 1527726.6965 | 662130.8864 | 1019643.0167 | 1527726.6965 | 1527726.6965 | 1.05 | 2.49 | 5.5898 | 5.5898 | 1674.7878 | 669.9151 | 984.6743 | 984.6743 | 0.4 | 0.58794 | 0.58794 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1077806.2308 | 1584212.8159 | 1584212.8159 | 680765.1463 | 1077806.2308 | 1584212.8159 | 1584212.8159 | 1.05 | 2.6319 | 5.6862 | 5.6862 | 1674.7321 | 669.8929 | 965.8698 | 965.8698 | 0.4 | 0.57673 | 0.57673 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1136137.1298 | 1638113.5811 | 1638113.5811 | 698955.5556 | 1136137.1298 | 1638113.5811 | 1638113.5811 | 1.05 | 2.7743 | 5.7674 | 5.7674
930 | 1673.0294 | 669.2118 | 1003.8176 | 1338.4235 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 220307.0803 | 330460.6204 | 440614.1605 | 307942.2653 | 0.55911 | 330460.6204 | 440614.1605 | 1.05 | 1.05 | 1.2092 | 2.1496 | 1672.9766 | 669.1906 | 1003.7859 | 1338.3813 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 275742.4054 | 413613.6081 | 551484.8107 | 344519.4235 | 0.49977 | 413613.6081 | 551484.8107 | 1.05 | 1.05 | 1.5134 | 2.6905 | 1672.9236 | 669.1694 | 1003.7541 | 1333.0791 | 0.4 | 0.6 | 0.79686 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 331323.1393 | 496984.7089 | 660042.0517 | 377654.5258 | 0.45593 | 496984.7089 | 660042.0517 | 1.05 | 1.05 | 1.8184 | 3.2073 | 1672.8705 | 669.1482 | 1003.7223 | 1293.8819 | 0.4 | 0.6 | 0.77345 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 387050.2965 | 580575.4447 | 748410.2645 | 408187.225 | 0.42184 | 580575.4447 | 748410.2645 | 1.05 | 1.05 | 2.1242 | 3.5298 | 1672.8172 | 669.1269 | 1003.6903 | 1257.8365 | 0.4 | 0.6 | 0.75193 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 442924.9033 | 664387.355 | 832618.0625 | 436664.2841 | 442924.9033 | 664387.355 | 832618.0625 | 1.05 | 1.0803 | 2.4307 | 3.8176 | 1672.7638 | 669.1055 | 1003.6583 | 1224.532 | 0.4 | 0.6 | 0.73204 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 498947.9985 | 748421.9978 | 913126.2646 | 463465.2733 | 498947.9985 | 748421.9978 | 913126.2646 | 1.05 | 1.2169 | 2.7381 | 4.0758 | 1672.7102 | 669.0841 | 1003.6261 | 1193.6263 | 0.4 | 0.6 | 0.71359 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 555120.6326 | 832680.9489 | 990318.909 | 488866.4064 | 555120.6326 | 832680.9489 | 990318.909 | 1.05 | 1.3539 | 3.0463 | 4.3088 | 1672.6565 | 669.0626 | 1003.5939 | 1164.8312 | 0.4 | 0.6 | 0.6964 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 611443.8685 | 917165.8028 | 1064517.6141 | 513076.0944 | 611443.8685 | 917165.8028 | 1064517.6141 | 1.05 | 1.4912 | 3.3552 | 4.5199 | 1672.6026 | 669.041 | 1003.5616 | 1137.9007 | 0.4 | 0.6 | 0.68032 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 667918.7812 | 1001878.1718 | 1135991.9852 | 536256.1714 | 667918.7812 | 1001878.1718 | 1135991.9852 | 1.05 | 1.6289 | 3.665 | 4.7119 | 1672.5486 | 669.0194 | 1003.5292 | 1112.6219 | 0.4 | 0.6 | 0.66523 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 724546.4579 | 1086819.6869 | 1204966.8574 | 558535.2744 | 724546.4579 | 1086819.6869 | 1204966.8574 | 1.05 | 1.7669 | 3.9756 | 4.887 | 1672.4944 | 668.9978 | 1003.4967 | 1088.8071 | 0.4 | 0.6 | 0.65101 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 781327.9981 | 1171991.9971 | 1271626.7303 | 580017.6545 | 781327.9981 | 1171991.9971 | 1271626.7303 | 1.05 | 1.9053 | 4.287 | 5.0469 | 1672.4401 | 668.9761 | 1003.4641 | 1066.2869 | 0.4 | 0.6 | 0.63756 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 838264.5134 | 1257396.77 | 1336117.2912 | 600789.1925 | 838264.5134 | 1257396.77 | 1336117.2912 | 1.05 | 2.0441 | 4.5993 | 5.1932 | 1672.3857 | 668.9543 | 1003.4314 | 1044.9032 | 0.4 | 0.6 | 0.6248 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 895357.1278 | 1343035.6917 | 1398543.2627 | 620921.6319 | 895357.1278 | 1343035.6917 | 1398543.2627 | 1.05 | 2.1833 | 4.9124 | 5.3268 | 1672.3311 | 668.9324 | 1003.3986 | 1024.5002 | 0.4 | 0.6 | 0.61262 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 952606.9777 | 1428910.4665 | 1458960.5852 | 640475.636 | 952606.9777 | 1428910.4665 | 1458960.5852 | 1.05 | 2.3228 | 5.2263 | 5.4484 | 1672.2763 | 668.9105 | 1003.3658 | 1004.9124 | 0.4 | 0.6 | 0.60092 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1010015.2117 | 1515022.8176 | 1517358.189 | 659503.0433 | 1010015.2117 | 1515022.8176 | 1517358.189 | 1.05 | 2.4627 | 5.5411 | 5.5582 | 1672.2214 | 668.8885 | 985.9417 | 985.9417 | 0.4 | 0.5896 | 0.5896 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1067582.9909 | 1573617.3385 | 1573617.3385 | 678048.5665 | 1067582.9909 | 1573617.3385 | 1573617.3385 | 1.05 | 2.603 | 5.6554 | 5.6554 | 1672.1663 | 668.8665 | 967.3076 | 967.3076 | 0.4 | 0.57848 | 0.57848 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1125311.4886 | 1627413.487 | 1627413.487 | 696151.0922 | 1125311.4886 | 1627413.487 | 1627413.487 | 1.05 | 2.7436 | 5.7382 | 5.7382
940 | 1670.4511 | 668.1804 | 1002.2707 | 1336.3609 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 218363.4045 | 327545.1068 | 436726.8091 | 306817.3443 | 0.56203 | 327545.1068 | 436726.8091 | 1.05 | 1.05 | 1.1967 | 2.1274 | 1670.3987 | 668.1595 | 1002.2392 | 1336.319 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 273299.3416 | 409949.0124 | 546598.6832 | 343254.3729 | 0.50239 | 409949.0124 | 546598.6832 | 1.05 | 1.05 | 1.4977 | 2.6625 | 1670.3462 | 668.1385 | 1002.2077 | 1332.8195 | 0.4 | 0.6 | 0.79793 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 328375.1657 | 492562.7486 | 655051.0493 | 376260.6178 | 0.45833 | 492562.7486 | 655051.0493 | 1.05 | 1.05 | 1.7994 | 3.1825 | 1670.2936 | 668.1174 | 1002.1761 | 1293.8165 | 0.4 | 0.6 | 0.7746 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 383591.8219 | 575387.7328 | 742829.6123 | 406672.7995 | 0.42407 | 575387.7328 | 742829.6123 | 1.05 | 1.05 | 2.1019 | 3.5033 | 1670.2408 | 668.0963 | 1002.1445 | 1257.9382 | 0.4 | 0.6 | 0.75315 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 438950.2658 | 658425.3987 | 826486.0797 | 435035.7785 | 438950.2658 | 658425.3987 | 826486.0797 | 1.05 | 1.069 | 2.4052 | 3.7897 | 1670.1879 | 668.0751 | 1002.1127 | 1224.7789 | 0.4 | 0.6 | 0.73332 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 494451.4639 | 741677.1959 | 906475.4397 | 461727.8087 | 494451.4639 | 741677.1959 | 906475.4397 | 1.05 | 1.2041 | 2.7092 | 4.047 | 1670.1348 | 668.0539 | 1002.0809 | 1194.0006 | 0.4 | 0.6 | 0.71491 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 550096.3934 | 825144.5901 | 983177.2293 | 487024.1488 | 550096.3934 | 825144.5901 | 983177.2293 | 1.05 | 1.3396 | 3.014 | 4.2791 | 1670.0816 | 668.0326 | 1002.049 | 1165.3184 | 0.4 | 0.6 | 0.69776 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 605886.0423 | 908829.0634 | 1056909.6436 | 511132.4912 | 605886.0423 | 908829.0634 | 1056909.6436 | 1.05 | 1.4754 | 3.3196 | 4.4895 | 1670.0283 | 668.0113 | 1002.017 | 1138.4892 | 0.4 | 0.6 | 0.68172 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 661821.4093 | 992732.1139 | 1127939.8009 | 534214.1129 | 661821.4093 | 992732.1139 | 1127939.8009 | 1.05 | 1.6115 | 3.626 | 4.6809 | 1669.9748 | 667.9899 | 1001.9849 | 1113.3027 | 0.4 | 0.6 | 0.66666 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 717903.5039 | 1076855.2559 | 1196490.9441 | 556397.2089 | 717903.5039 | 1076855.2559 | 1196490.9441 | 1.05 | 1.748 | 3.9331 | 4.8555 | 1669.9211 | 667.9685 | 1001.9527 | 1089.5734 | 0.4 | 0.6 | 0.65247 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 774133.3467 | 1161200.02 | 1262746.9515 | 577785.6722 | 774133.3467 | 1161200.02 | 1262746.9515 | 1.05 | 1.8849 | 4.241 | 5.0152 | 1669.8674 | 667.9469 | 1001.9204 | 1067.1347 | 0.4 | 0.6 | 0.63905 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 830511.9687 | 1245767.953 | 1326854.1044 | 598465.0892 | 830511.9687 | 1245767.953 | 1326854.1044 | 1.05 | 2.0221 | 4.5497 | 5.1613 | 1669.8134 | 667.9254 | 1001.8881 | 1045.8312 | 0.4 | 0.6 | 0.62632 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 887040.412 | 1330560.6181 | 1388919.4674 | 618506.9572 | 887040.412 | 1330560.6181 | 1388919.4674 | 1.05 | 2.1597 | 4.8593 | 5.2949 | 1669.7594 | 667.9037 | 1001.8556 | 1025.5114 | 0.4 | 0.6 | 0.61417 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 943719.7298 | 1415579.5947 | 1449004.1776 | 637971.7312 | 943719.7298 | 1415579.5947 | 1449004.1776 | 1.05 | 2.2976 | 5.1696 | 5.4166 | 1669.7051 | 667.8821 | 1001.8231 | 1006.0158 | 0.4 | 0.6 | 0.60251 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1000550.9857 | 1500826.4785 | 1507107.5954 | 656911.0717 | 1000550.9857 | 1500826.4785 | 1507107.5954 | 1.05 | 2.4359 | 5.4807 | 5.5267 | 1669.6508 | 667.8603 | 987.1576 | 987.1576 | 0.4 | 0.59124 | 0.59124 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1057535.2546 | 1563132.2808 | 1563132.2808 | 675369.5373 | 1057535.2546 | 1563132.2808 | 1563132.2808 | 1.05 | 2.5745 | 5.6247 | 5.6247 | 1669.5962 | 667.8385 | 968.6802 | 968.6802 | 0.4 | 0.58019 | 0.58019 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1114673.6221 | 1616801.4335 | 1616801.4335 | 693385.8802 | 1114673.6221 | 1616801.4335 | 1616801.4335 | 1.05 | 2.7135 | 5.7089 | 5.7089
950 | 1667.8688 | 667.1475 | 1000.7213 | 1334.295 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 216447.957 | 324671.9355 | 432895.914 | 305705.0896 | 0.56495 | 324671.9355 | 432895.914 | 1.05 | 1.05 | 1.1843 | 2.1055 | 1667.8169 | 667.1267 | 1000.6901 | 1334.2535 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 270892.1349 | 406338.2023 | 541784.2698 | 342003.7587 | 0.505 | 406338.2023 | 541784.2698 | 1.05 | 1.05 | 1.4822 | 2.635 | 1667.7648 | 667.1059 | 1000.6589 | 1332.5309 | 0.4 | 0.6 | 0.79899 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 325470.9166 | 488206.375 | 650121.7236 | 374882.8296 | 0.46073 | 488206.375 | 650121.7236 | 1.05 | 1.05 | 1.7808 | 3.1578 | 1667.7127 | 667.0851 | 1000.6276 | 1293.7208 | 0.4 | 0.6 | 0.77575 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 380185.183 | 570277.7745 | 737317.4599 | 405176.1201 | 0.42629 | 570277.7745 | 737317.4599 | 1.05 | 1.05 | 2.0801 | 3.477 | 1667.6604 | 667.0641 | 1000.5962 | 1258.0085 | 0.4 | 0.6 | 0.75436 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 435035.8243 | 652553.7365 | 820429.0115 | 433426.6074 | 435035.8243 | 652553.7365 | 820429.0115 | 1.05 | 1.0578 | 2.3801 | 3.7622 | 1667.6079 | 667.0432 | 1000.5648 | 1224.9935 | 0.4 | 0.6 | 0.73458 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 490023.7404 | 735035.6106 | 899905.6195 | 460011.2421 | 490023.7404 | 735035.6106 | 899905.6195 | 1.05 | 1.1915 | 2.6808 | 4.0183 | 1667.5554 | 667.0221 | 1000.5332 | 1194.3418 | 0.4 | 0.6 | 0.71622 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 545149.8406 | 817724.7609 | 976122.373 | 485204.3377 | 545149.8406 | 817724.7609 | 976122.373 | 1.05 | 1.3255 | 2.9823 | 4.2496 | 1667.5027 | 667.0011 | 1000.5016 | 1165.7719 | 0.4 | 0.6 | 0.69911 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 600415.0437 | 900622.5656 | 1049394.0714 | 509212.8749 | 600415.0437 | 900622.5656 | 1049394.0714 | 1.05 | 1.4598 | 3.2846 | 4.4593 | 1667.4498 | 666.9799 | 1000.4699 | 1139.0434 | 0.4 | 0.6 | 0.68311 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 655820.2783 | 983730.4174 | 1119985.345 | 532197.5794 | 655820.2783 | 983730.4174 | 1119985.345 | 1.05 | 1.5945 | 3.5875 | 4.6502 | 1667.3968 | 666.9587 | 1000.4381 | 1113.9484 | 0.4 | 0.6 | 0.66808 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 711366.4822 | 1067049.7233 | 1188117.8093 | 554286.2086 | 711366.4822 | 1067049.7233 | 1188117.8093 | 1.05 | 1.7294 | 3.8913 | 4.8244 | 1667.3437 | 666.9375 | 1000.4062 | 1090.304 | 0.4 | 0.6 | 0.65392 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 767054.6031 | 1150581.9047 | 1253974.6362 | 575582.3016 | 767054.6031 | 1150581.9047 | 1253974.6362 | 1.05 | 1.8648 | 4.1957 | 4.9837 | 1667.2905 | 666.9162 | 1000.3743 | 1067.9457 | 0.4 | 0.6 | 0.64053 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 822885.5981 | 1234328.3972 | 1317702.5333 | 596171.153 | 822885.5981 | 1234328.3972 | 1317702.5333 | 1.05 | 2.0004 | 4.501 | 5.1296 | 1667.2371 | 666.8948 | 1000.3422 | 1046.7211 | 0.4 | 0.6 | 0.62782 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 878860.434 | 1318290.651 | 1379410.5945 | 616124.0171 | 878860.434 | 1318290.651 | 1379410.5945 | 1.05 | 2.1365 | 4.807 | 5.2631 | 1667.1835 | 666.8734 | 1000.3101 | 1026.4824 | 0.4 | 0.6 | 0.6157 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 934980.0871 | 1402470.1306 | 1439164.5547 | 635501.1425 | 934980.0871 | 1402470.1306 | 1439164.5547 | 1.05 | 2.2728 | 5.1138 | 5.3849 | 1667.1299 | 666.8519 | 1000.2779 | 1007.0757 | 0.4 | 0.6 | 0.60408 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 991245.5432 | 1486868.3148 | 1496972.9937 | 654354.0139 | 991245.5432 | 1486868.3148 | 1496972.9937 | 1.05 | 2.4095 | 5.4214 | 5.4953 | 1667.076 | 666.8304 | 988.3243 | 988.3243 | 0.4 | 0.59285 | 0.59285 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1047657.798 | 1552757.0618 | 1552757.0618 | 672727.0376 | 1047657.798 | 1552757.0618 | 1552757.0618 | 1.05 | 2.5465 | 5.5939 | 5.5939 | 1667.0221 | 666.8088 | 969.9916 | 969.9916 | 0.4 | 0.58187 | 0.58187 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1104217.8567 | 1606280.6214 | 1606280.6214 | 690658.8335 | 1104217.8567 | 1606280.6214 | 1606280.6214 | 1.05 | 2.6839 | 5.6794 | 5.6794
960 | 1665.2824 | 666.113 | 999.1694 | 1332.2259 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 214560.0908 | 321840.1362 | 429120.1816 | 304605.2529 | 0.56787 | 321840.1362 | 429120.1816 | 1.05 | 1.05 | 1.1722 | 2.0839 | 1665.231 | 666.0924 | 999.1386 | 1332.1848 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 268519.9484 | 402779.9225 | 537039.8967 | 340767.2907 | 0.50762 | 402779.9225 | 537039.8967 | 1.05 | 1.05 | 1.4669 | 2.6079 | 1665.1794 | 666.0718 | 999.1076 | 1332.1435 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 322609.353 | 483914.0296 | 645218.7061 | 373520.8295 | 0.46312 | 483914.0296 | 645218.7061 | 1.05 | 1.05 | 1.7624 | 3.1331 | 1665.1277 | 666.0511 | 999.0766 | 1293.5953 | 0.4 | 0.6 | 0.77687 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 376829.1262 | 565243.6893 | 731872.3653 | 403696.8132 | 0.42852 | 565243.6893 | 731872.3653 | 1.05 | 1.05 | 2.0585 | 3.451 | 1665.0759 | 666.0303 | 999.0455 | 1258.048 | 0.4 | 0.6 | 0.75555 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 431180.0976 | 646770.1465 | 814445.2614 | 431836.3543 | 0.40061 | 646770.1465 | 814445.2614 | 1.05 | 1.05 | 2.3553 | 3.7349 | 1665.0239 | 666.0096 | 999.0144 | 1225.1764 | 0.4 | 0.6 | 0.73583 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 485663.1055 | 728494.6583 | 893415.0549 | 458315.1136 | 485663.1055 | 728494.6583 | 893415.0549 | 1.05 | 1.179 | 2.6529 | 3.99 | 1664.9718 | 665.9887 | 998.9831 | 1194.6506 | 0.4 | 0.6 | 0.71752 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 540278.9965 | 810418.4947 | 969152.4407 | 483406.4682 | 540278.9965 | 810418.4947 | 969152.4407 | 1.05 | 1.3116 | 2.9511 | 4.2204 | 1664.9196 | 665.9679 | 998.9518 | 1166.1922 | 0.4 | 0.6 | 0.70045 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 595028.6256 | 892542.9383 | 1041968.8502 | 507316.6946 | 595028.6256 | 892542.9383 | 1041968.8502 | 1.05 | 1.4445 | 3.25 | 4.4294 | 1664.8673 | 665.9469 | 998.9204 | 1139.5638 | 0.4 | 0.6 | 0.68448 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 649912.8564 | 974869.2845 | 1112126.4278 | 530205.9725 | 649912.8564 | 974869.2845 | 1112126.4278 | 1.05 | 1.5776 | 3.5497 | 4.6196 | 1664.8148 | 665.9259 | 998.8889 | 1114.5598 | 0.4 | 0.6 | 0.66948 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 704932.5608 | 1057398.8412 | 1179845.1314 | 552201.6265 | 704932.5608 | 1057398.8412 | 1179845.1314 | 1.05 | 1.7112 | 3.8501 | 4.7934 | 1664.7622 | 665.9049 | 998.8573 | 1090.9994 | 0.4 | 0.6 | 0.65535 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 760088.6194 | 1140132.9291 | 1245307.3502 | 573406.845 | 760088.6194 | 1140132.9291 | 1245307.3502 | 1.05 | 1.845 | 4.1512 | 4.9524 | 1664.7095 | 665.8838 | 998.8257 | 1068.7207 | 0.4 | 0.6 | 0.64199 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 815381.9209 | 1223072.8814 | 1308660.0684 | 593906.6344 | 815381.9209 | 1223072.8814 | 1308660.0684 | 1.05 | 1.9791 | 4.4531 | 5.0981 | 1664.6566 | 665.8626 | 998.7939 | 1047.5737 | 0.4 | 0.6 | 0.6293 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 870813.3628 | 1306220.0441 | 1370014.1292 | 613772.0079 | 870813.3628 | 1306220.0441 | 1370014.1292 | 1.05 | 2.1136 | 4.7556 | 5.2315 | 1664.6036 | 665.8414 | 998.7621 | 1027.4142 | 0.4 | 0.6 | 0.61721 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 926383.8507 | 1389575.7761 | 1429439.3368 | 633063.0108 | 926383.8507 | 1389575.7761 | 1429439.3368 | 1.05 | 2.2484 | 5.0589 | 5.3534 | 1664.5504 | 665.8202 | 998.7302 | 1008.0935 | 0.4 | 0.6 | 0.60563 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 982094.2991 | 1473141.4487 | 1486952.4349 | 651830.9533 | 982094.2991 | 1473141.4487 | 1486952.4349 | 1.05 | 2.3836 | 5.363 | 5.464 | 1664.4971 | 665.7988 | 989.4436 | 989.4436 | 0.4 | 0.59444 | 0.59444 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1037945.6306 | 1542490.86 | 1542490.86 | 670120.0916 | 1037945.6306 | 1542490.86 | 1542490.86 | 1.05 | 2.519 | 5.5633 | 5.5633 | 1664.4437 | 665.7775 | 971.2456 | 971.2456 | 0.4 | 0.58353 | 0.58353 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1093938.7764 | 1595853.3138 | 1595853.3138 | 687968.9145 | 1093938.7764 | 1595853.3138 | 1595853.3138 | 1.05 | 2.6548 | 5.6499 | 5.6499
970 | 1662.692 | 665.0768 | 997.6152 | 1330.1536 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 212699.1795 | 319048.7693 | 425398.359 | 303517.593 | 0.57079 | 319048.7693 | 425398.359 | 1.05 | 1.05 | 1.1602 | 2.0626 | 1662.641 | 665.0564 | 997.5846 | 1330.1128 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 266181.9723 | 399272.9585 | 532363.9446 | 339544.6876 | 0.51024 | 399272.9585 | 532363.9446 | 1.05 | 1.05 | 1.4519 | 2.5811 | 1662.5899 | 665.036 | 997.5539 | 1330.0719 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 319789.4706 | 479684.2059 | 639578.9412 | 372174.296 | 0.46552 | 479684.2059 | 639578.9412 | 1.05 | 1.05 | 1.7442 | 3.1009 | 1662.5386 | 665.0155 | 997.5232 | 1293.4404 | 0.4 | 0.6 | 0.77799 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 373522.4407 | 560283.661 | 726492.9317 | 402234.5169 | 0.43075 | 560283.661 | 726492.9317 | 1.05 | 1.05 | 2.0373 | 3.4253 | 1662.4873 | 664.9949 | 997.4924 | 1258.0571 | 0.4 | 0.6 | 0.75673 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 427381.6563 | 641072.4844 | 808533.2841 | 430264.6166 | 0.4027 | 641072.4844 | 808533.2841 | 1.05 | 1.05 | 2.3309 | 3.7078 | 1662.4358 | 664.9743 | 997.4615 | 1225.3281 | 0.4 | 0.6 | 0.73707 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 481367.8985 | 722051.8477 | 887002.0544 | 456638.9786 | 481367.8985 | 722051.8477 | 887002.0544 | 1.05 | 1.1668 | 2.6253 | 3.9618 | 1662.3842 | 664.9537 | 997.4305 | 1194.9274 | 0.4 | 0.6 | 0.7188 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 535481.956 | 803222.934 | 962265.5964 | 481630.0532 | 535481.956 | 803222.934 | 962265.5964 | 1.05 | 1.2979 | 2.9203 | 4.1913 | 1662.3325 | 664.933 | 997.3995 | 1166.58 | 0.4 | 0.6 | 0.70177 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 589724.625 | 884586.9374 | 1034632.0026 | 505443.4192 | 589724.625 | 884586.9374 | 1034632.0026 | 1.05 | 1.4294 | 3.2161 | 4.3996 | 1662.2806 | 664.9123 | 997.3684 | 1140.051 | 0.4 | 0.6 | 0.68584 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 644096.7089 | 966145.0633 | 1104360.9357 | 528238.7162 | 644096.7089 | 966145.0633 | 1104360.9357 | 1.05 | 1.5611 | 3.5125 | 4.5893 | 1662.2287 | 664.8915 | 997.3372 | 1115.1373 | 0.4 | 0.6 | 0.67087 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 698599.0187 | 1047898.5281 | 1171670.6702 | 550142.8399 | 698599.0187 | 1047898.5281 | 1171670.6702 | 1.05 | 1.6931 | 3.8096 | 4.7627 | 1662.1765 | 664.8706 | 997.3059 | 1091.6603 | 0.4 | 0.6 | 0.65677 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 753232.3731 | 1129848.5597 | 1236742.7444 | 571258.632 | 753232.3731 | 1129848.5597 | 1236742.7444 | 1.05 | 1.8255 | 4.1074 | 4.9213 | 1662.1243 | 664.8497 | 997.2746 | 1069.4603 | 0.4 | 0.6 | 0.64343 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 807997.5979 | 1211996.3969 | 1299724.285 | 591670.8134 | 807997.5979 | 1211996.3969 | 1299724.285 | 1.05 | 1.9582 | 4.4059 | 5.0668 | 1662.0719 | 664.8288 | 997.2432 | 1048.3898 | 0.4 | 0.6 | 0.63077 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 862895.5265 | 1294343.2897 | 1360727.6343 | 611450.1588 | 862895.5265 | 1294343.2897 | 1360727.6343 | 1.05 | 2.0911 | 4.7051 | 5.2001 | 1662.0194 | 664.8078 | 997.2117 | 1028.3078 | 0.4 | 0.6 | 0.61871 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 917926.9997 | 1376890.4996 | 1419826.1963 | 630656.5123 | 917926.9997 | 1376890.4996 | 1419826.1963 | 1.05 | 2.2244 | 5.005 | 5.322 | 1661.9668 | 664.7867 | 997.1801 | 1009.0704 | 0.4 | 0.6 | 0.60715 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 973092.8659 | 1459639.2989 | 1477043.9571 | 649341.0118 | 973092.8659 | 1459639.2989 | 1477043.9571 | 1.05 | 2.358 | 5.3056 | 5.4329 | 1661.914 | 664.7656 | 990.5173 | 990.5173 | 0.4 | 0.59601 | 0.59601 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1028393.9807 | 1532332.6663 | 1532332.6663 | 667547.7649 | 1028393.9807 | 1532332.6663 | 1532332.6663 | 1.05 | 2.492 | 5.5326 | 5.5326 | 1661.8611 | 664.7445 | 972.4451 | 972.4451 | 0.4 | 0.58515 | 0.58515 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1083831.2074 | 1585521.0383 | 1585521.0383 | 685315.131 | 1083831.2074 | 1585521.0383 | 1585521.0383 | 1.05 | 2.6262 | 5.6202 | 5.6202
980 | 1660.0975 | 664.039 | 996.0585 | 1328.078 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 210864.6163 | 316296.9245 | 421729.2326 | 302441.8755 | 0.57372 | 316296.9245 | 421729.2326 | 1.05 | 1.05 | 1.1484 | 2.0416 | 1660.0469 | 664.0188 | 996.0282 | 1328.0375 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 263877.4231 | 395816.1346 | 527754.8461 | 338335.6764 | 0.51287 | 395816.1346 | 527754.8461 | 1.05 | 1.05 | 1.4371 | 2.5548 | 1659.9963 | 663.9985 | 995.9978 | 1327.997 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 317010.2981 | 475515.4472 | 634020.5962 | 370842.9176 | 0.46793 | 475515.4472 | 634020.5962 | 1.05 | 1.05 | 1.7264 | 3.0691 | 1659.9455 | 663.9782 | 995.9673 | 1293.2567 | 0.4 | 0.6 | 0.7791 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 370263.9566 | 555395.9349 | 721177.8053 | 400788.881 | 0.43298 | 555395.9349 | 721177.8053 | 1.05 | 1.05 | 2.0163 | 3.3997 | 1659.8946 | 663.9578 | 995.9368 | 1258.0363 | 0.4 | 0.6 | 0.7579 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 423639.1203 | 635458.6804 | 802691.5832 | 428711.0049 | 0.40479 | 635458.6804 | 802691.5832 | 1.05 | 1.05 | 2.3069 | 3.6809 | 1659.8436 | 663.9374 | 995.9062 | 1225.449 | 0.4 | 0.6 | 0.73829 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 477136.5175 | 715704.7762 | 880664.9811 | 454982.4077 | 477136.5175 | 715704.7762 | 880664.9811 | 1.05 | 1.1547 | 2.5982 | 3.9339 | 1659.7925 | 663.917 | 995.8755 | 1195.1728 | 0.4 | 0.6 | 0.72007 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 530756.8832 | 796135.3248 | 955460.0651 | 479874.6222 | 530756.8832 | 796135.3248 | 955460.0651 | 1.05 | 1.2845 | 2.8901 | 4.1625 | 1659.7412 | 663.8965 | 995.8447 | 1166.9357 | 0.4 | 0.6 | 0.70308 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 584500.959 | 876751.4385 | 1027381.6184 | 503592.5365 | 584500.959 | 876751.4385 | 1027381.6184 | 1.05 | 1.4145 | 3.1826 | 4.3701 | 1659.6898 | 663.8759 | 995.8139 | 1140.5056 | 0.4 | 0.6 | 0.68718 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 638369.493 | 957554.2395 | 1096686.8279 | 526295.2551 | 638369.493 | 957554.2395 | 1096686.8279 | 1.05 | 1.5448 | 3.4758 | 4.5593 | 1659.6384 | 663.8553 | 995.783 | 1115.6816 | 0.4 | 0.6 | 0.67224 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 692363.2399 | 1038544.8598 | 1163592.2629 | 548109.2494 | 692363.2399 | 1038544.8598 | 1163592.2629 | 1.05 | 1.6754 | 3.7697 | 4.7321 | 1659.5867 | 663.8347 | 995.752 | 1092.2874 | 0.4 | 0.6 | 0.65817 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 746482.9609 | 1119724.4413 | 1228278.5508 | 569137.0175 | 746482.9609 | 1119724.4413 | 1228278.5508 | 1.05 | 1.8063 | 4.0642 | 4.8905 | 1659.535 | 663.814 | 995.721 | 1070.1652 | 0.4 | 0.6 | 0.64486 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 800729.4239 | 1201094.1359 | 1290892.8395 | 589462.9978 | 800729.4239 | 1201094.1359 | 1290892.8395 | 1.05 | 1.9375 | 4.3594 | 5.0357 | 1659.4831 | 663.7932 | 995.6899 | 1049.1701 | 0.4 | 0.6 | 0.63223 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 855103.4034 | 1282655.105 | 1351548.7465 | 609157.7294 | 855103.4034 | 1282655.105 | 1351548.7465 | 1.05 | 2.069 | 4.6553 | 5.1688 | 1659.4311 | 663.7725 | 995.6587 | 1029.164 | 0.4 | 0.6 | 0.62019 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 909605.6801 | 1364408.5202 | 1410322.859 | 628280.8568 | 909605.6801 | 1364408.5202 | 1410322.859 | 1.05 | 2.2008 | 4.9519 | 5.2908 | 1659.379 | 663.7516 | 995.6274 | 1010.0075 | 0.4 | 0.6 | 0.60867 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 964237.0418 | 1446355.5626 | 1467245.5965 | 646883.3477 | 964237.0418 | 1446355.5626 | 1467245.5965 | 1.05 | 2.3329 | 5.2491 | 5.4019 | 1659.3268 | 663.7307 | 991.5472 | 991.5472 | 0.4 | 0.59756 | 0.59756 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1018998.2822 | 1522281.3251 | 1522281.3251 | 665009.1627 | 1018998.2822 | 1522281.3251 | 1522281.3251 | 1.05 | 2.4654 | 5.502 | 5.502 | 1659.2744 | 663.7098 | 973.5929 | 973.5929 | 0.4 | 0.58676 | 0.58676 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1073890.2021 | 1575284.7415 | 1575284.7415 | 682696.5333 | 1073890.2021 | 1575284.7415 | 1575284.7415 | 1.05 | 2.5981 | 5.5905 | 5.5905
990 | 1657.4989 | 662.9996 | 994.4993 | 1325.9991 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 209055.8131 | 313583.7196 | 418111.6262 | 301377.873 | 0.57665 | 313583.7196 | 418111.6262 | 1.05 | 1.05 | 1.1368 | 2.0209 | 1657.4488 | 662.9795 | 994.4693 | 1325.959 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 261605.5419 | 392408.3128 | 523211.0838 | 337139.9921 | 0.51549 | 392408.3128 | 523211.0838 | 1.05 | 1.05 | 1.4225 | 2.5288 | 1657.3986 | 662.9594 | 994.4391 | 1325.9189 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 314270.896 | 471406.3439 | 628541.7919 | 369526.3924 | 0.47033 | 471406.3439 | 628541.7919 | 1.05 | 1.05 | 1.7088 | 3.0379 | 1657.3483 | 662.9393 | 994.409 | 1293.0445 | 0.4 | 0.6 | 0.78019 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 367052.5431 | 550578.8146 | 715925.6734 | 399359.5663 | 0.43521 | 550578.8146 | 715925.6734 | 1.05 | 1.05 | 1.9957 | 3.3744 | 1657.2978 | 662.9191 | 994.3787 | 1257.986 | 0.4 | 0.6 | 0.75906 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 419951.1568 | 629926.7352 | 796918.7088 | 427175.1422 | 0.40688 | 629926.7352 | 796918.7088 | 1.05 | 1.05 | 2.2833 | 3.6543 | 1657.2473 | 662.8989 | 994.3484 | 1225.5396 | 0.4 | 0.6 | 0.7395 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 472967.4165 | 709451.1248 | 874402.2504 | 453344.9858 | 472967.4165 | 709451.1248 | 874402.2504 | 1.05 | 1.1429 | 2.5714 | 3.9062 | 1657.1966 | 662.8786 | 994.318 | 1195.3872 | 0.4 | 0.6 | 0.72133 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 526102.0075 | 789153.0113 | 948734.1296 | 478139.721 | 526102.0075 | 789153.0113 | 948734.1296 | 1.05 | 1.2712 | 2.8602 | 4.134 | 1657.1458 | 662.8583 | 994.2875 | 1167.2599 | 0.4 | 0.6 | 0.70438 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 579355.6208 | 869033.4312 | 1020215.8504 | 501763.5522 | 579355.6208 | 869033.4312 | 1020215.8504 | 1.05 | 1.3999 | 3.1497 | 4.3409 | 1657.0949 | 662.838 | 994.2569 | 1140.9281 | 0.4 | 0.6 | 0.68851 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 632728.9532 | 949093.4298 | 1089102.132 | 524375.0539 | 632728.9532 | 949093.4298 | 1089102.132 | 1.05 | 1.5288 | 3.4397 | 4.5294 | 1657.0439 | 662.8176 | 994.2263 | 1116.1933 | 0.4 | 0.6 | 0.67361 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 686222.7074 | 1029334.0611 | 1155607.8204 | 546100.2773 | 686222.7074 | 1029334.0611 | 1155607.8204 | 1.05 | 1.658 | 3.7304 | 4.7018 | 1656.9928 | 662.7971 | 994.1957 | 1092.8811 | 0.4 | 0.6 | 0.65956 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 739837.5917 | 1109756.3875 | 1219912.5779 | 567041.3806 | 739837.5917 | 1109756.3875 | 1219912.5779 | 1.05 | 1.7874 | 4.0218 | 4.8598 | 1656.9415 | 662.7766 | 994.1649 | 1070.836 | 0.4 | 0.6 | 0.64627 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 793574.3203 | 1190361.4804 | 1282163.4656 | 587282.5224 | 793574.3203 | 1190361.4804 | 1282163.4656 | 1.05 | 1.9172 | 4.3137 | 5.0047 | 1656.8901 | 662.756 | 994.1341 | 1049.9153 | 0.4 | 0.6 | 0.63367 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 847433.6131 | 1271150.4196 | 1342475.1749 | 606894.0082 | 847433.6131 | 1271150.4196 | 1342475.1749 | 1.05 | 2.0473 | 4.6064 | 5.1378 | 1656.8386 | 662.7355 | 994.1032 | 1029.9838 | 0.4 | 0.6 | 0.62166 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 901416.1958 | 1352124.2937 | 1400927.1048 | 625935.2855 | 901416.1958 | 1352124.2937 | 1400927.1048 | 1.05 | 2.1776 | 4.8996 | 5.2597 | 1656.787 | 662.7148 | 994.0722 | 1010.9058 | 0.4 | 0.6 | 0.61016 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 955522.7999 | 1433284.1998 | 1457555.3969 | 644457.1534 | 955522.7999 | 1433284.1998 | 1457555.3969 | 1.05 | 2.3083 | 5.1936 | 5.371 | 1656.7353 | 662.6941 | 992.5345 | 992.5345 | 0.4 | 0.59909 | 0.59909 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1009754.1624 | 1512335.5678 | 1512335.5678 | 662503.4272 | 1009754.1624 | 1512335.5678 | 1512335.5678 | 1.05 | 2.4392 | 5.4715 | 5.4715 | 1656.6834 | 662.6734 | 974.6914 | 974.6914 | 0.4 | 0.58834 | 0.58834 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1064111.0263 | 1565144.909 | 1565144.909 | 680112.2119 | 1064111.0263 | 1565144.909 | 1565144.909 | 1.05 | 2.5704 | 5.5608 | 5.5608
1000 | 1654.8962 | 661.9585 | 992.9377 | 1323.9169 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 207272.1998 | 310908.2998 | 414544.3997 | 300325.3643 | 0.57958 | 310908.2998 | 414544.3997 | 1.05 | 1.05 | 1.1253 | 2.0005 | 1654.8465 | 661.9386 | 992.9079 | 1323.8772 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 259365.5938 | 389048.3907 | 518731.1876 | 335957.3774 | 0.51812 | 389048.3907 | 518731.1876 | 1.05 | 1.05 | 1.4081 | 2.5033 | 1654.7968 | 661.9187 | 992.8781 | 1323.8374 | 0.4 | 0.6 | 0.8 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | < 0.8 f.n.c Velocity Basis | 311570.3548 | 467355.5322 | 623140.7096 | 368224.4273 | 0.47273 | 467355.5322 | 623140.7096 | 1.05 | 1.05 | 1.6914 | 3.007 | 1654.7469 | 661.8988 | 992.8481 | 1292.8042 | 0.4 | 0.6 | 0.78127 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 363887.1066 | 545830.6599 | 710735.2629 | 397946.2441 | 0.43744 | 545830.6599 | 710735.2629 | 1.05 | 1.05 | 1.9754 | 3.3493 | 1654.6969 | 661.8788 | 992.8181 | 1257.9066 | 0.4 | 0.6 | 0.7602 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 416316.478 | 624474.717 | 791213.2555 | 425656.6636 | 0.40897 | 624474.717 | 791213.2555 | 1.05 | 1.05 | 2.26 | 3.6279 | 1654.6468 | 661.8587 | 992.7881 | 1225.6004 | 0.4 | 0.6 | 0.7407 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 468859.103 | 703288.6545 | 868212.3276 | 451726.3112 | 468859.103 | 703288.6545 | 868212.3276 | 1.05 | 1.1312 | 2.5451 | 3.8787 | 1654.5966 | 661.8386 | 992.7579 | 1195.5711 | 0.4 | 0.6 | 0.72258 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 521515.6209 | 782273.4313 | 942086.1278 | 476424.9107 | 521515.6209 | 782273.4313 | 942086.1278 | 1.05 | 1.2582 | 2.8309 | 4.1056 | 1654.5463 | 661.8185 | 992.7278 | 1167.553 | 0.4 | 0.6 | 0.70566 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 574286.6757 | 861430.0135 | 1013132.912 | 499955.9889 | 574286.6757 | 861430.0135 | 1013132.912 | 1.05 | 1.3854 | 3.1172 | 4.3118 | 1654.4958 | 661.7983 | 992.6975 | 1141.319 | 0.4 | 0.6 | 0.68983 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 627172.9168 | 940759.3752 | 1081604.9414 | 522477.5961 | 627172.9168 | 940759.3752 | 1081604.9414 | 1.05 | 1.513 | 3.4042 | 4.4998 | 1654.4453 | 661.7781 | 992.6672 | 1116.6727 | 0.4 | 0.6 | 0.67495 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 680174.9987 | 1020262.4981 | 1147715.3234 | 544115.367 | 680174.9987 | 1020262.4981 | 1147715.3234 | 1.05 | 1.6408 | 3.6917 | 4.6717 | 1654.3946 | 661.7578 | 992.6368 | 1093.4421 | 0.4 | 0.6 | 0.66093 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 733293.5808 | 1099940.3712 | 1211642.7078 | 564971.1232 | 733293.5808 | 1099940.3712 | 1211642.7078 | 1.05 | 1.7689 | 3.9799 | 4.8293 | 1654.3438 | 661.7375 | 992.6063 | 1071.4734 | 0.4 | 0.6 | 0.64767 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 786529.3277 | 1179793.9916 | 1273533.9711 | 585128.7463 | 786529.3277 | 1179793.9916 | 1273533.9711 | 1.05 | 1.8972 | 4.2687 | 4.974 | 1654.2929 | 661.7172 | 992.5758 | 1050.6262 | 0.4 | 0.6 | 0.63509 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 839882.909 | 1259824.3636 | 1333504.6978 | 604658.311 | 839882.909 | 1259824.3636 | 1333504.6978 | 1.05 | 2.0258 | 4.5582 | 5.1069 | 1654.2419 | 661.6968 | 992.5452 | 1030.7678 | 0.4 | 0.6 | 0.62311 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 893354.9994 | 1340032.499 | 1391636.7679 | 623619.0693 | 893354.9994 | 1340032.499 | 1391636.7679 | 1.05 | 2.1548 | 4.8482 | 5.2288 | 1654.1908 | 661.6763 | 992.5145 | 1011.7664 | 0.4 | 0.6 | 0.61164 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 946946.2783 | 1420419.4175 | 1447971.4166 | 642061.6536 | 946946.2783 | 1420419.4175 | 1447971.4166 | 1.05 | 2.2839 | 5.1389 | 5.3402 | 1654.1395 | 661.6558 | 992.4837 | 993.4808 | 0.4 | 0.6 | 0.6006 | < 0.4 f.n.c Velocity Basis | < 0.6 f.n.c Velocity Basis | Dynamic stress check basis | 1000657.4307 | 1500986.146 | 1502494.0395 | 660029.7354 | 1000657.4307 | 1500986.146 | 1502494.0395 | 1.05 | 2.4134 | 5.4302 | 5.4411 | 1654.0882 | 661.6353 | 975.7427 | 975.7427 | 0.4 | 0.5899 | 0.5899 | < 0.4 f.n.c Velocity Basis | Dynamic stress check basis | Dynamic stress check basis | 1054489.1459 | 1555101.6581 | 1555101.6581 | 677561.2945 | 1054489.1459 | 1555101.6581 | 1555101.6581 | 1.05 | 2.5432 | 5.5311 | 5.5311